## Sheet1
结构体名 | 描述 | 变量名 | 变量描述 | 索引 | 子索引 | 数据类型 | 系数 | 数据长度 | 读写权限 | PDO ID
POWER_PARAMETER | 测量数据 | Total_AB_Voltage | AB线电压 | 0x2000 | 0x01 | uint16_t | 100 | 2 | readonly | -
|  | Total_BC_Voltage | BC线电压 |  | 0x02 | uint16_t | 100 | 2 | readonly | -
|  | Total_AC_Voltage | CA线电压 |  | 0x03 | uint16_t | 100 | 2 | readonly | -
|  | LA_result->Voltage | A相电压 |  | 0x04 | uint16_t | 100 | 2 | readonly | -
|  | LB_result->Voltage | B相电压 |  | 0x05 | uint16_t | 100 | 2 | readonly | -
|  | LC_result->Voltage | C相电压 |  | 0x06 | uint16_t | 100 | 2 | readonly | -
|  | Voltage_N | N相电压 |  | 0x07 | uint16_t | 100 | 2 | readonly | -
|  | LA_result->Current | A相电流 |  | 0x08 | uint32_t | 100 | 4 | readonly | -
|  | LB_result->Current | B相电流 |  | 0x09 | uint32_t | 100 | 4 | readonly | -
|  | LC_result->Current | C相电流 |  | 0x0a | uint32_t | 100 | 4 | readonly | -
|  | Total_Creepage | 漏电流 |  | 0x0b | uint16_t | 10 | 2 | readonly | -
|  | Current_Ground | 接地电流 |  | 0x0c | uint16_t | 10 | 2 | readonly | -
|  | Total_Electric_Quantity | 总电量 |  | 0x0d | uint32_t | 100 | 4 | readonly | -
|  | LA_result->Active_Energy | A有功电量 |  | 0x0e | uint32_t | 100 | 4 | readonly | -
|  | LB_result->Active_Energy | B有功电量 |  | 0x0f | uint32_t | 100 | 4 | readonly | -
|  | LC_result->Active_Energy | C有功电量 |  | 0x10 | uint32_t | 100 | 4 | readonly | -
|  | LA_result->Reactive_Energy | A无功电量 |  | 0x11 | uint32_t | 100 | 4 | readonly | -
|  | LB_result->Reactive_Energy | B无功电量 |  | 0x12 | uint32_t | 100 | 4 | readonly | -
|  | LC_result->Reactive_Energy | C无功电量 |  | 0x13 | uint32_t | 100 | 4 | readonly | -
|  | Total_Active_Power[4] | 总有功功率 |  | 0x14 | 4*uint8_t | 100 | 4 | readonly | -
|  | LA_result->Active_Power[4] | A相有功功率 |  | 0x15 | 4*uint8_t | 100 | 4 | readonly | -
|  | LB_result->Active_Power[4] | B相有功功率 |  | 0x16 | 4*uint8_t | 100 | 4 | readonly | -
|  | LC_result->Active_Power[4] | C相有功功率 |  | 0x17 | 4*uint8_t | 100 | 4 | readonly | -
|  | Total_Reactive_Power[4] | 总无功功率 |  | 0x18 | 4*uint8_t | 100 | 4 | readonly | -
|  | LA_result->Reactive_Power[4] | A相无功功率 |  | 0x19 | 4*uint8_t | 100 | 4 | readonly | -
|  | LB_result->Reactive_Power[4] | B相无功功率 |  | 0x1a | 4*uint8_t | 100 | 4 | readonly | -
|  | LC_result->Reactive_Power[4] | C相无功功率 |  | 0x1b | 4*uint8_t | 100 | 4 | readonly | -
|  | Total_Apparent_Power[4] | 总视在功率 |  | 0x1c | 4*uint8_t | 100 | 4 | readonly | -
|  | LA_result->Apparent_Power[4] | A相视在功率 |  | 0x1d | 4*uint8_t | 100 | 4 | readonly | -
|  | LB_result->Apparent_Power[4] | B相视在功率 |  | 0x1e | 4*uint8_t | 100 | 4 | readonly | -
|  | LC_result->Apparent_Power[4] | C相视在功率 |  | 0x1f | 4*uint8_t | 100 | 4 | readonly | -
|  | Total_Power_Factor | 总功率因数 |  | 0x20 | uint8_t | 100 | 1 | readonly | -
|  | LA_result->Power_Factor | A相功率因数 |  | 0x21 | uint8_t | 100 | 1 | readonly | -
|  | LB_result->Power_Factor | B相功率因数 |  | 0x22 | uint8_t | 100 | 1 | readonly | -
|  | LC_result->Power_Factor | C相功率因数 |  | 0x23 | uint8_t | 100 | 1 | readonly | -
|  | LA_result->Angle | A相相位角 |  | 0x24 | uint16_t | 1 | 2 | readonly | -
|  | LB_result->Angle | B相相位角 |  | 0x25 | uint16_t | 1 | 2 | readonly | -
|  | LC_result->Angle | C相相位角 |  | 0x26 | uint16_t | 1 | 4 | readonly | -
|  | LA_result->Voltage_wave | 基波A相电压 |  | 0x27 | uint16_t | 100 | 4 | readonly | -
|  | LB_result->Voltage_wave | 基波B相电压 |  | 0x28 | uint16_t | 100 | 2 | readonly | -
|  | LC_result->Voltage_wave | 基波C相电压 |  | 0x29 | uint16_t | 100 | 2 | readonly | -
|  | LA_result->Current_wave | 基波A相电流 |  | 0x2a | uint32_t | 100 | 4 | readonly | -
|  | LB_result->Current_wave | 基波B相电流 |  | 0x2b | uint32_t | 100 | 4 | readonly | -
|  | LC_result->Current_wave | 基波C相电流 |  | 0x2c | uint32_t | 100 | 4 | readonly | -
|  | Temp | 温度 |  | 0x2d | int16_t | 10 | 2 | readonly | -
DEVICE_SET_PARAMETER | 保护数据 | Kr | 反时限过载脱扣等级 | 0x2001 | 0x01 | uint8_t | 1 | 1 | readwrite | -
|  | E_Kr | 反时限过载tE 脱扣等级 |  | 0x02 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_INVVERSE_OVERLOAD] | 反时限过载启动门限值 |  | 0x03 | uint16_t | 1 | 2 | readwrite | -
|  | overload_recov_en | 反时限过载自动复位 |  | 0x04 | uint8_t | 1 | 1 | readwrite | -
|  | overload_cool_time | 反时限过载冷却时间 |  | 0x05 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_threshold[ZT_INVVERSE_OVERLOAD] | 反时限过载报警门限值 |  | 0x06 | uint16_t | 1 | 2 | readwrite | -
|  | overload_startshield_time | 反时限过载起动屏蔽时间 |  | 0x07 | uint8_t | 1 | 1 | readwrite | -
|  | run_en[ZT_INVVERSE_OVERLOAD] | 反时限过载运行阶段 |  | 0x08 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_INVVERSE_OVERLOAD] | 反时限过载起动阶段 |  | 0x09 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_INVVERSE_OVERLOAD] | 反时限过载脱扣使能 |  | 0x0a | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_INVVERSE_OVERLOAD] | 反时限过载报警使能 |  | 0x0b | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣门限值 |  | 0x0c | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣延时 |  | 0x0d | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_CONSTANT_OVERLOAD] | 定时限过载报警值 |  | 0x0e | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_CONSTANT_OVERLOAD] | 定时限过载报警延时 |  | 0x0f | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_CONSTANT_OVERLOAD] | 定时限过载运行阶段 |  | 0x10 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_CONSTANT_OVERLOAD] | 定时限过载起动阶段 |  | 0x11 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣使能 |  | 0x12 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_CONSTANT_OVERLOAD] | 定时限过载报警使能 |  | 0x13 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_UNDERLOAD] | 欠载脱扣门限值 |  | 0x14 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_UNDERLOAD] | 欠载脱扣延时 |  | 0x15 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_UNDERLOAD] | 欠载报警值 |  | 0x16 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_UNDERLOAD] | 欠载报警延时 |  | 0x17 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_UNDERLOAD] | 欠载运行阶段 |  | 0x18 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_UNDERLOAD] | 欠载起动阶段 |  | 0x19 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_UNDERLOAD] | 欠载脱扣使能 |  | 0x1a | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_UNDERLOAD] | 欠载报警使能 |  | 0x1b | uint8_t | 1 | 1 | readwrite | -
|  | short_start_protect | 短路启动脱扣值 |  | 0x1c | uint16_t | 1 | 2 | readwrite | -
|  | protect_threshold[ZT_SHORT_CIRCUIT] | 短路运行脱扣值 |  | 0x1d | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_SHORT_CIRCUIT] | 短路脱扣延时 |  | 0x1e | uint16_t | 1 | 2 | readwrite | -
|  | short_start_alarm | 短路启动报警值 |  | 0x1f | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_SHORT_CIRCUIT] | 短路运行报警值 |  | 0x20 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_SHORT_CIRCUIT] | 短路报警延时 |  | 0x21 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_SHORT_CIRCUIT] | 短路运行阶段 |  | 0x22 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_SHORT_CIRCUIT] | 短路起动阶段 |  | 0x23 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_SHORT_CIRCUIT] | 短路脱扣使能 |  | 0x24 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_SHORT_CIRCUIT] | 短路报警使能 |  | 0x25 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_LOCKEDROTOR] | 堵转脱扣门限值 |  | 0x26 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_LOCKEDROTOR] | 堵转脱扣延时 |  | 0x27 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_LOCKEDROTOR] | 堵转报警值 |  | 0x28 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_LOCKEDROTOR] | 堵转报警延时 |  | 0x29 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_LOCKEDROTOR] | 堵转脱扣使能 |  | 0x2a | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_LOCKEDROTOR] | 堵转报警使能 |  | 0x2b | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_BLOCK] | 阻塞脱扣门限值 |  | 0x2c | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_BLOCK] | 阻塞脱扣延时 |  | 0x2d | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_BLOCK] | 阻塞报警门限值 |  | 0x2e | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_BLOCK] | 阻塞报警延时 |  | 0x2f | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_BLOCK] | 阻塞脱扣使能 |  | 0x30 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_BLOCK] | 阻塞报警使能 |  | 0x31 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_LACK] | 断相脱扣延时 |  | 0x32 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_LACK] | 断相报警延时 |  | 0x33 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_LACK] | 断相脱扣使能 |  | 0x34 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_LACK] | 断相报警使能 |  | 0x35 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣门限值 |  | 0x36 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣延时 |  | 0x37 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_CURRENT_IMBALANCE] | 电流不平衡报警值 |  | 0x38 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_CURRENT_IMBALANCE] | 电流不平衡报警延时 |  | 0x39 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_CURRENT_IMBALANCE] | 电流不平衡运行阶段 |  | 0x3a | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_CURRENT_IMBALANCE] | 电流不平衡起动阶段 |  | 0x3b | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣使能 |  | 0x3c | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_CURRENT_IMBALANCE] | 电流不平衡报警使能 |  | 0x3d | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_OVERPOWER] | 过功率脱扣门限值 |  | 0x3e | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_OVERPOWER] | 过功率脱扣延时 |  | 0x3f | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_OVERPOWER] | 过功率报警值 |  | 0x40 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_OVERPOWER] | 过功率报警延时 |  | 0x41 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_OVERPOWER] | 过功率运行阶段 |  | 0x42 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_OVERPOWER] | 过功率起动阶段 |  | 0x43 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_OVERPOWER] | 过功率脱扣使能 |  | 0x44 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_OVERPOWER] | 过功率报警使能 |  | 0x45 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_UNDERPOWER] | 欠功率脱扣门限值 |  | 0x46 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_UNDERPOWER] | 欠功率脱扣延时 |  | 0x47 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_UNDERPOWER] | 欠功率报警值 |  | 0x48 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_UNDERPOWER] | 欠功率报警延时 |  | 0x49 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_UNDERPOWER] | 欠功率运行阶段 |  | 0x4a | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_UNDERPOWER] | 欠功率起动阶段 |  | 0x4b | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_UNDERPOWER] | 欠功率脱扣使能 |  | 0x4c | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_UNDERPOWER] | 欠功率报警使能 |  | 0x4d | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_GROUND] | 接地脱扣门限值 |  | 0x4e | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_GROUND] | 接地脱扣延时 |  | 0x4f | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_GROUND] | 接地报警值 |  | 0x50 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_GROUND] | 接地报警延时 |  | 0x51 | uint16_t | 1 | 2 | readwrite | -
|  | ground_startshield_time | 接地起动屏蔽时间 |  | 0x52 | uint8_t | 1 | 1 | readwrite | -
|  | ground_trip_type | 接地脱扣方式 |  | 0x53 | uint8_t | 1 | 1 | readwrite | -
|  | run_en[ZT_GROUND] | 接地运行阶段 |  | 0x54 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_GROUND] | 接地起动阶段 |  | 0x55 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_GROUND] | 接地脱扣使能 |  | 0x56 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_GROUND] | 接地报警使能 |  | 0x57 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_LEAKAGE] | 漏电脱扣门限值 |  | 0x58 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_LEAKAGE] | 漏电脱扣延时 |  | 0x59 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_LEAKAGE] | 漏电报警值 |  | 0x5a | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_LEAKAGE] | 漏电报警延时 |  | 0x5b | uint16_t | 1 | 2 | readwrite | -
|  | leakage_startshield_time | 漏电起动屏蔽时间 |  | 0x5c | uint8_t | 1 | 1 | readwrite | -
|  | leakage_trip_type | 漏电脱扣方式 |  | 0x5d | uint8_t | 1 | 1 | readwrite | -
|  | run_en[ZT_LEAKAGE] | 漏电运行阶段 |  | 0x5e | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_LEAKAGE] | 漏电起动阶段 |  | 0x5f | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_LEAKAGE] | 漏电脱扣使能 |  | 0x60 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_LEAKAGE] | 漏电报警使能 |  | 0x61 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_BREAK] | 溢出保护门限值 |  | 0x62 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_BREAK] | 溢出脱扣使能 |  | 0x63 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_BREAK] | 溢出报警使能 |  | 0x64 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_PHASE] | 相序脱扣延时 |  | 0x65 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_PHASE] | 相序报警延时 |  | 0x66 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_PHASE] | 相序脱扣使能 |  | 0x67 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_PHASE] | 相序报警使能 |  | 0x68 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_OVERVOLTAGE] | 过电压脱扣门限值 |  | 0x69 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_OVERVOLTAGE] | 过电压脱扣延时 |  | 0x6a | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_OVERVOLTAGE] | 过电压报警值 |  | 0x6b | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_OVERVOLTAGE] | 过电压报警延时 |  | 0x6c | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_OVERVOLTAGE] | 过电压运行阶段 |  | 0x6d | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_OVERVOLTAGE] | 过电压起动阶段 |  | 0x6e | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_OVERVOLTAGE] | 过电压脱扣使能 |  | 0x6f | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_OVERVOLTAGE] | 过电压报警使能 |  | 0x70 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_UNDERVOLTAGE] | 欠电压脱扣门限值 |  | 0x71 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_UNDERVOLTAGE] | 欠电压脱扣延时 |  | 0x72 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_UNDERVOLTAGE] | 欠电压报警值 |  | 0x73 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_UNDERVOLTAGE] | 欠电压报警延时 |  | 0x74 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_UNDERVOLTAGE] | 欠电压运行阶段 |  | 0x75 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_UNDERVOLTAGE] | 欠电压起动阶段 |  | 0x76 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_UNDERVOLTAGE] | 欠电压脱扣使能 |  | 0x77 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_UNDERVOLTAGE] | 欠电压报警使能 |  | 0x78 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣门限值 |  | 0x79 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣延时 |  | 0x7a | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_VOLTAGE_IMBALANCE] | 电压不平衡报警值 |  | 0x7b | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_VOLTAGE_IMBALANCE] | 电压不平衡报警延时 |  | 0x7c | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_VOLTAGE_IMBALANCE] | 电压不平衡运行阶段 |  | 0x7d | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_VOLTAGE_IMBALANCE] | 电压不平衡起动阶段 |  | 0x7e | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣使能 |  | 0x7f | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_VOLTAGE_IMBALANCE] | 电压不平衡报警使能 |  | 0x80 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_START_TIMEOUT] | 超时电流 |  | 0x81 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_START_TIMEOUT] | 起动超时动作延时 |  | 0x82 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_START_TIMEOUT] | 起动超时脱扣使能 |  | 0x83 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_START_TIMEOUT] | 起动超时报警使能 |  | 0x84 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_START_NUMBER] | 超时次数 |  | 0x85 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_START_NUMBER] | 时间范围 |  | 0x86 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_START_NUMBER] | 超时次数脱扣使能 |  | 0x87 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_START_NUMBER] | 超时次数报警使能 |  | 0x88 | uint8_t | 1 | 1 | readwrite | -
|  | temp_type | 温度传感器类型 |  | 0x89 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_TH] | 温度脱扣门限值 |  | 0x8a | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_TH] | 温度脱扣延时 |  | 0x8b | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_TH] | 温度报警值 |  | 0x8c | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_TH] | 温度报警延时 |  | 0x8d | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_TH] | 温度运行阶段 |  | 0x8e | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_TH] | 温度起动阶段 |  | 0x8f | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_TH] | 温度脱扣使能 |  | 0x90 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_TH] | 温度报警使能 |  | 0x91 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_EXTERNAL] | 外部故障脱扣延时 |  | 0x92 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_EXTERNAL] | 外部故障报警延时 |  | 0x93 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_EXTERNAL] | 外部故障运行阶段 |  | 0x94 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_EXTERNAL] | 外部故障起动阶段 |  | 0x95 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_EXTERNAL] | 外部故障脱扣使能 |  | 0x96 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_EXTERNAL] | 外部故障报警使能 |  | 0x97 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_INSULATION] | 绝缘故障脱扣延时 |  | 0x98 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_INSULATION] | 绝缘故障报警延时 |  | 0x99 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_INSULATION] | 绝缘故障运行阶段 |  | 0x9a | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_INSULATION] | 绝缘故障起动阶段 |  | 0x9b | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_INSULATION] | 绝缘故障脱扣使能 |  | 0x9c | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_INSULATION] | 绝缘故障报警使能 |  | 0x9d | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_RUN_TIMEOUT] | 运行超时报警时长 |  | 0x9e | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_RUN_TIMEOUT] | 运行超时脱扣使能 |  | 0x9f | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_RUN_TIMEOUT] | 运行超时报警使能 |  | 0xa0 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_FAIL_NUMBER] | 故障次数 |  | 0xa1 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_en[ZT_FAIL_NUMBER] | 故障次数报警使能 |  | 0xa2 | uint8_t | 1 | 1 | readwrite | -
|  | Kr_H | 反时限过载脱扣等级（高速） |  | 0xa3 | uint8_t | 1 | 1 | readwrite | -
|  | E_Kr_H | 反时限过载tE 脱扣等级（高速） |  | 0xa4 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载启动门限值（高速） |  | 0xa5 | uint16_t | 1 | 2 | readwrite | -
|  | overload_recov_en_hight | 反时限过载自动复位（高速） |  | 0xa6 | uint8_t | 1 | 1 | readwrite | -
|  | overload_cool_time_hight | 反时限过载冷却时间（高速） |  | 0xa7 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_threshold[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载报警门限值（高速） |  | 0xa8 | uint16_t | 1 | 2 | readwrite | -
|  | overload_startshield_time_hight | 反时限过载起动屏蔽时间（高速） |  | 0xa9 | uint8_t | 1 | 1 | readwrite | -
|  | run_en[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载运行阶段（高速） |  | 0xaa | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载起动阶段（高速） |  | 0xab | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载脱扣使能（高速） |  | 0xac | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载报警使能（高速） |  | 0xad | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣门限值（高速） |  | 0xae | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣延时（高速） |  | 0xaf | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载报警值（高速） |  | 0xb0 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载报警延时（高速） |  | 0xb1 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载运行阶段（高速） |  | 0xb2 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载起动阶段（高速） |  | 0xb3 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣使能（高速） |  | 0xb4 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载报警使能（高速） |  | 0xb5 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_UNDERLOAD_HIGH] | 欠载脱扣门限值（高速） |  | 0xb6 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_UNDERLOAD_HIGH] | 欠载脱扣延时（高速） |  | 0xb7 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_UNDERLOAD_HIGH] | 欠载报警值（高速） |  | 0xb8 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_UNDERLOAD_HIGH] | 欠载报警延时（高速） |  | 0xb9 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_UNDERLOAD_HIGH] | 欠载运行阶段（高速） |  | 0xba | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_UNDERLOAD_HIGH] | 欠载起动阶段（高速） |  | 0xbb | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_UNDERLOAD_HIGH] | 欠载脱扣使能（高速） |  | 0xbc | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_UNDERLOAD_HIGH] | 欠载报警使能（高速） |  | 0xbd | uint8_t | 1 | 1 | readwrite | -
|  | short_start_protect_hight | 短路启动脱扣值（高速） |  | 0xbe | uint16_t | 1 | 2 | readwrite | -
|  | protect_threshold[ZT_SHORT_CIRCUIT_HIGH] | 短路运行脱扣值（高速） |  | 0xbf | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_SHORT_CIRCUIT_HIGH] | 短路脱扣延时（高速） |  | 0xc0 | uint16_t | 1 | 2 | readwrite | -
|  | short_start_alarm_hight | 短路启动报警值（高速） |  | 0xc1 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_SHORT_CIRCUIT_HIGH] | 短路运行报警值（高速） |  | 0xc2 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_SHORT_CIRCUIT_HIGH] | 短路报警延时（高速） |  | 0xc3 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_SHORT_CIRCUIT_HIGH] | 短路运行阶段（高速） |  | 0xc4 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_SHORT_CIRCUIT_HIGH] | 短路起动阶段（高速） |  | 0xc5 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_SHORT_CIRCUIT_HIGH] | 短路脱扣使能（高速） |  | 0xc6 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_SHORT_CIRCUIT_HIGH] | 短路报警使能（高速） |  | 0xc7 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣门限值（高速） |  | 0xc8 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣延时（高速） |  | 0xc9 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_LOCKEDROTOR_HIGH] | 堵转报警值（高速） |  | 0xca | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_LOCKEDROTOR_HIGH] | 堵转报警延时（高速） |  | 0xcb | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣使能（高速） |  | 0xcc | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_LOCKEDROTOR_HIGH] | 堵转报警使能（高速） |  | 0xcd | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_BLOCK_HIGH] | 阻塞脱扣门限值（高速） |  | 0xce | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_BLOCK_HIGH] | 阻塞脱扣延时（高速） |  | 0xcf | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_BLOCK_HIGH] | 阻塞报警门限值（高速） |  | 0xd0 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_BLOCK_HIGH] | 阻塞报警延时（高速） |  | 0xd1 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_BLOCK_HIGH] | 阻塞脱扣使能（高速） |  | 0xd2 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_BLOCK_HIGH] | 阻塞报警使能（高速） |  | 0xd3 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_LACK_HIGH] | 断相脱扣延时（高速） |  | 0xd4 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_LACK_HIGH] | 断相报警延时（高速） |  | 0xd5 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_LACK_HIGH] | 断相脱扣使能（高速） |  | 0xd6 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_LACK_HIGH] | 断相报警使能（高速） |  | 0xd7 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣门限值（高速） |  | 0xd8 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣延时（高速） |  | 0xd9 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡报警值（高速） |  | 0xda | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡报警延时（高速） |  | 0xdb | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡运行阶段（高速） |  | 0xdc | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡起动阶段（高速） |  | 0xdd | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣使能（高速） |  | 0xde | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡报警使能（高速） |  | 0xdf | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_OVERPOWER_HIGH] | 过功率脱扣门限值（高速） |  | 0xe0 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_OVERPOWER_HIGH] | 过功率脱扣延时（高速） |  | 0xe1 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_OVERPOWER_HIGH] | 过功率报警值（高速） |  | 0xe2 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_OVERPOWER_HIGH] | 过功率报警延时（高速） |  | 0xe3 | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_OVERPOWER_HIGH] | 过功率运行阶段（高速） |  | 0xe4 | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_OVERPOWER_HIGH] | 过功率起动阶段（高速） |  | 0xe5 | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_OVERPOWER_HIGH] | 过功率脱扣使能（高速） |  | 0xe6 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_OVERPOWER_HIGH] | 过功率报警使能（高速） |  | 0xe7 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_UNDERPOWER_HIGH] | 欠功率脱扣门限值（高速） |  | 0xe8 | uint16_t | 1 | 2 | readwrite | -
|  | protect_delay[ZT_UNDERPOWER_HIGH] | 欠功率脱扣延时（高速） |  | 0xe9 | uint16_t | 1 | 2 | readwrite | -
|  | alarm_threshold[ZT_UNDERPOWER_HIGH] | 欠功率报警值（高速） |  | 0xea | uint16_t | 1 | 2 | readwrite | -
|  | alarm_delay[ZT_UNDERPOWER_HIGH] | 欠功率报警延时（高速） |  | 0xeb | uint16_t | 1 | 2 | readwrite | -
|  | run_en[ZT_UNDERPOWER_HIGH] | 欠功率运行阶段（高速） |  | 0xec | uint8_t | 1 | 1 | readwrite | -
|  | start_en[ZT_UNDERPOWER_HIGH] | 欠功率起动阶段（高速） |  | 0xed | uint8_t | 1 | 1 | readwrite | -
|  | protect_en[ZT_UNDERPOWER_HIGH] | 欠功率脱扣使能（高速） |  | 0xee | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_UNDERPOWER_HIGH] | 欠功率报警使能（高速） |  | 0xef | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_ANALOG1] | 模拟量1输入保护门限 |  | 0xf0 | uint16_t | 1 | 2 | readwrite | -
|  | analog_type[0] | 模拟量1输入保护类型 |  | 0xf1 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_ANALOG1] | 模拟量1输入动作时间 |  | 0xf2 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_ANALOG1] | 模拟量1输入脱扣使能 |  | 0xf3 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_ANALOG1] | 模拟量1输入报警使能 |  | 0xf4 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_ANALOG2] | 模拟量2输入保护门限 |  | 0xf5 | uint16_t | 1 | 2 | readwrite | -
|  | analog_type[1] | 模拟量2输入保护类型 |  | 0xf6 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_ANALOG2] | 模拟量2输入动作时间 |  | 0xf7 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_ANALOG2] | 模拟量2输入脱扣使能 |  | 0xf8 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_ANALOG2] | 模拟量2输入报警使能 |  | 0xf9 | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_ANALOG3] | 模拟量3输入保护门限 |  | 0xfa | uint16_t | 1 | 2 | readwrite | -
|  | analog_type[2] | 模拟量3输入保护类型 |  | 0xfb | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_ANALOG3] | 模拟量3输入动作时间 |  | 0xfc | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_ANALOG3] | 模拟量3输入脱扣使能 |  | 0xfd | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_ANALOG3] | 模拟量3输入报警使能 |  | 0xfe | uint8_t | 1 | 1 | readwrite | -
|  | protect_threshold[ZT_ANALOG4] | 模拟量4输入保护门限 |  | 0xff | uint16_t | 1 | 2 | readwrite | -
|  | analog_type[3] | 模拟量4输入保护类型 |  | 0x100 | uint8_t | 1 | 1 | readwrite | -
|  | protect_delay[ZT_ANALOG4] | 模拟量4输入动作时间 |  | 0x101 | uint16_t | 1 | 2 | readwrite | -
|  | protect_en[ZT_ANALOG4] | 模拟量4输入脱扣使能 |  | 0x102 | uint8_t | 1 | 1 | readwrite | -
|  | alarm_en[ZT_ANALOG4] | 模拟量4输入报警使能 |  | 0x103 | uint8_t | 1 | 1 | readwrite | -
CONTROL_PARAMETER | 控制命令 | start1 | 起动1 | 0x2003 | 0x01 | uint16 | 1 | 2 | writeonly | -
|  | start2 | 起动2 |  | 0x02 | uint16 | 1 | 2 | writeonly | -
|  | start3 | 起动3 |  | 0x03 | uint16 | 1 | 2 | writeonly | -
|  | stop | 停机 |  | 0x04 | uint16 | 1 | 2 | writeonly | -
|  | reset | 复位 |  | 0x05 | uint16 | 1 | 2 | writeonly | -
|  | powerclear | 电量清零 |  | 0x06 | uint16 | 1 | 2 | writeonly | -
|  | eventclear | 事件总清 |  | 0x07 | uint16 | 1 | 2 | writeonly | -
FaultRecord | 保护动作事件 | usReason | (上1次)故障原因 | 0x2004 | 0x01 | uint16 | 1 | 2 | readonly | -
|  | usPhase | (上1次)故障相别 |  | 0x02 | uint16 | 1 | 2 | readonly | -
|  | ucDateTime | (上1次)跳闸发生时刻 |  | 0x03 | uint8 | 1 | 6 | readonly | -
|  | fUa | (上1次)跳闸前A相电压 |  | 0x04 | float | 10 | 4 | readonly | -
|  | fUb | (上1次)跳闸前B相电压 |  | 0x05 | float | 10 | 4 | readonly | -
|  | fUc | (上1次)跳闸前C相电压 |  | 0x06 | float | 10 | 4 | readonly | -
|  | fIa | (上1次)跳闸前A相电流 |  | 0x07 | float | 10 | 4 | readonly | -
|  | fIb | (上1次)跳闸前B相电流 |  | 0x08 | float | 10 | 4 | readonly | -
|  | fIc | (上1次)跳闸前C相电流 |  | 0x09 | float | 10 | 4 | readonly | -
|  | usCurDirection | (上1次)跳闸前三相电流方向 |  | 0x0a | uint16 | 1 | 2 | readonly | -
|  | usReason | (上2次)故障原因 | 0x2005 | 0x01 | uint16 | 1 | 2 | readonly | -
|  | usPhase | (上2次)故障相别 |  | 0x02 | uint16 | 1 | 2 | readonly | -
|  | ucDateTime | (上2次)跳闸发生时刻 |  | 0x03 | uint8 | 1 | 6 | readonly | -
|  | fUa | (上2次)跳闸前A相电压 |  | 0x04 | float | 10 | 4 | readonly | -
|  | fUb | (上2次)跳闸前B相电压 |  | 0x05 | float | 10 | 4 | readonly | -
|  | fUc | (上2次)跳闸前C相电压 |  | 0x06 | float | 10 | 4 | readonly | -
|  | fIa | (上2次)跳闸前A相电流 |  | 0x07 | float | 10 | 4 | readonly | -
|  | fIb | (上2次)跳闸前B相电流 |  | 0x08 | float | 10 | 4 | readonly | -
|  | fIc | (上2次)跳闸前C相电流 |  | 0x09 | float | 10 | 4 | readonly | -
|  | usCurDirection | (上2次)跳闸前三相电流方向 |  | 0x0a | uint16 | 1 | 2 | readonly | -
|  | ……………………………………… | [6 empty] | readonly | -
|  | usReason | (上20次)故障原因 | 0x2017 | 0x01 | uint16 | 1 | 2 | readonly | -
|  | usPhase | (上20次)故障相别 |  | 0x02 | uint16 | 1 | 2 | readonly | -
|  | ucDateTime | (上20次)跳闸发生时刻 |  | 0x03 | uint8 | 1 | 6 | readonly | -
|  | fUa | (上20次)跳闸前A相电压 |  | 0x04 | float | 10 | 4 | readonly | -
|  | fUb | (上20次)跳闸前B相电压 |  | 0x05 | float | 10 | 4 | readonly | -
|  | fUc | (上20次)跳闸前C相电压 |  | 0x06 | float | 10 | 4 | readonly | -
|  | fIa | (上20次)跳闸前A相电流 |  | 0x07 | float | 10 | 4 | readonly | -
|  | fIb | (上20次)跳闸前B相电流 |  | 0x08 | float | 10 | 4 | readonly | -
|  | fIc | (上20次)跳闸前C相电流 |  | 0x09 | float | 10 | 4 | readonly | -
|  | usCurDirection | (上20次)跳闸前三相电流方向 |  | 0x0a | uint16 | 1 | 2 | readonly | -

## 数据定义
结构体名 | 结构体描述 | 变量名 | 变量描述 | 数据类型 | 系数 | 数据长度 | 键值 | 最小值 | 最大值 | 默认值 | 单位 | 备注 | 修改点
POWER_PARAMETER | 测量数据 | Total_AB_Voltage | AB线电压 | uint16_t | 10 | 2 | 1 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | Total_BC_Voltage | BC线电压 | uint16_t | 10 | 2 | 2 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | Total_AC_Voltage | CA线电压 | uint16_t | 10 | 2 | 3 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | LA_result->Voltage | A相电压 | uint16_t | 10 | 2 | 4 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | LB_result->Voltage | B相电压 | uint16_t | 10 | 2 | 5 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | LC_result->Voltage | C相电压 | uint16_t | 10 | 2 | 6 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | Voltage_N | N相电压 | uint16_t | 10 | 2 | 7 | - | - | - | V | - | 原先为100 现改成10（防止数据溢出）
|  | LA_result->Current | A相电流 | float | 1 | 4 | 8 | - | - | - | A | 取两位小数点 | 原先为100 现改成10（防止数据溢出）
|  | LB_result->Current | B相电流 | float | 1 | 4 | 9 | - | - | - | A | 取两位小数点
|  | LC_result->Current | C相电流 | float | 1 | 4 | 10 | - | - | - | A | 取两位小数点
|  | Total_Creepage | 漏电流 | float | 1 | 4 | 11 | - | - | - | mA | 取两位小数点
|  | Current_Ground | 接地电流 | float | 1 | 4 | 12 | - | - | - | A | 取两位小数点
|  | Total_Electric_Quantity | 总电量 | float | 1 | 4 | 13 | - | - | - | KWh | 取两位小数点
|  | LA_result->Active_Energy | A有功电量 | float | 1 | 4 | 14 | - | - | - | KWh | 取两位小数点
|  | LB_result->Active_Energy | B有功电量 | float | 1 | 4 | 15 | - | - | - | KWh | 取两位小数点
|  | LC_result->Active_Energy | C有功电量 | float | 1 | 4 | 16 | - | - | - | KWh | 取两位小数点
|  | LA_result->Reactive_Energy | A无功电量 | float | 1 | 4 | 17 | - | - | - | KWh | 取两位小数点
|  | LB_result->Reactive_Energy | B无功电量 | float | 1 | 4 | 18 | - | - | - | KWh | 取两位小数点
|  | LC_result->Reactive_Energy | C无功电量 | float | 1 | 4 | 19 | - | - | - | KWh | 取两位小数点
|  | Total_Active_Power | 总有功功率 | float | 1 | 4 | 20 | - | - | - | kvar | 取两位小数点
|  | LA_result->Active_Power | A相有功功率 | float | 1 | 4 | 21 | - | - | - | kvar | 取两位小数点
|  | LB_result->Active_Power | B相有功功率 | float | 1 | 4 | 22 | - | - | - | kvar | 取两位小数点
|  | LC_result->Active_Power | C相有功功率 | float | 1 | 4 | 23 | - | - | - | kvar | 取两位小数点
|  | Total_Reactive_Power | 总无功功率 | float | 1 | 4 | 24 | - | - | - | kvar | 取两位小数点
|  | LA_result->Reactive_Power | A相无功功率 | float | 1 | 4 | 25 | - | - | - | kvar | 取两位小数点
|  | LB_result->Reactive_Power | B相无功功率 | float | 1 | 4 | 26 | - | - | - | kvar | 取两位小数点
|  | LC_result->Reactive_Power | C相无功功率 | float | 1 | 4 | 27 | - | - | - | kvar | 取两位小数点
|  | Total_Apparent_Power | 总视在功率 | float | 1 | 4 | 28 | - | - | - | kvar | 取两位小数点
|  | LA_result->Apparent_Power | A相视在功率 | float | 1 | 4 | 29 | - | - | - | kvar | 取两位小数点
|  | LB_result->Apparent_Power | B相视在功率 | float | 1 | 4 | 30 | - | - | - | kvar | 取两位小数点
|  | LC_result->Apparent_Power | C相视在功率 | float | 1 | 4 | 31 | - | - | - | kvar | 取两位小数点
|  | Total_Power_Factor | 总功率因数 | float | 1 | 4 | 32 | - | - | - | - | -
|  | LA_result->Power_Factor | A相功率因数 | float | 1 | 4 | 33 | - | - | - | - | -
|  | LB_result->Power_Factor | B相功率因数 | float | 1 | 4 | 34 | - | - | - | - | -
|  | LC_result->Power_Factor | C相功率因数 | float | 1 | 4 | 35 | - | - | - | - | -
|  | LA_result->Angle[0] | A相相位角 | uint16_t | 1 | 2 | 36 | - | - | - | - | -
|  | LB_result->Angle[0] | B相相位角 | uint16_t | 1 | 2 | 37 | - | - | - | - | -
|  | LC_result->Angle[0] | C相相位角 | uint16_t | 1 | 2 | 38 | - | - | - | - | -
|  | LA_result->Voltage_wave | 基波A相电压 | uint16_t | 10 | 2 | 39 | - | - | - | V | -
|  | LB_result->Voltage_wave | 基波B相电压 | uint16_t | 10 | 2 | 40 | - | - | - | V | -
|  | LC_result->Voltage_wave | 基波C相电压 | uint16_t | 10 | 2 | 41 | - | - | - | V | -
|  | LA_result->Current_wave | 基波A相电流 | float | 1 | 4 | 42 | - | - | - | A | -
|  | LB_result->Current_wave | 基波B相电流 | float | 1 | 4 | 43 | - | - | - | A | -
|  | LC_result->Current_wave | 基波C相电流 | float | 1 | 4 | 44 | - | - | - | A | -
|  | LA_result->harmonic_voltage | A相电压谐波 | uint8_t | 1 | 2 | 46
|  | LB_result->harmonic_voltage | B相电压谐波 | uint8_t | 1 | 2 | 47
|  | LC_result->harmonic_voltage | C相电压谐波 | uint8_t | 1 | 2 | 48
|  | LA_result->harmonic_current | A相电流谐波 | uint8_t | 1 | 2 | 49
|  | LB_result->harmonic_current | B相电流谐波 | uint8_t | 1 | 2 | 50
|  | LC_result->harmonic_current | C相电流谐波 | uint8_t | 1 | 2 | 51
|  | LA_result->harmonic_power | A相功率谐波 | uint8_t | 1 | 2 | 52
|  | LB_result->harmonic_power | B相功率谐波 | uint8_t | 1 | 2 | 53
|  | LC_result->harmonic_power | C相功率谐波 | uint8_t | 1 | 2 | 54
|  | DI_state[0] | DI0状态 | uint8_t | 1 | 2 | 55 | - | - | - | -
|  | DI_state[1] | DI1状态 | uint8_t | 1 | 2 | 56 | - | - | - | - | 0：打开 1：关闭
|  | DI_state[2] | DI2状态 | uint8_t | 1 | 2 | 57 | - | - | - | - | 0：打开 1：关闭
|  | DI_state[3] | DI3状态 | uint8_t | 1 | 2 | 58 | - | - | - | - | 0：打开 1：关闭
|  | DI_state[4] | DI4状态 | uint8_t | 1 | 2 | 59 | - | - | - | - | 0：打开 1：关闭
|  | DI_state[5] | DI5状态 | uint8_t | 1 | 2 | 60 | - | - | - | - | 0：打开 1：关闭
|  | DO_state[0] | DO0状态 | uint8_t | 1 | 2 | 61 | - | - | - | - | 0：打开 1：关闭
|  | DO_state[1] | DO1状态 | uint8_t | 1 | 2 | 62 | - | - | - | - | 0：打开 1：关闭
|  | DO_state[2] | DO2状态 | uint8_t | 1 | 2 | 63 | - | - | - | - | 0：打开 1：关闭
|  | DO_state[3] | DO3状态 | uint8_t | 1 | 2 | 64 | - | - | - | - | 0：打开 1：关闭
|  | LA_result->Angle[1] | A相电流相位角 | uint16_t | 1 | 2 | 38 | - | - | - | - |  | 新增电流相角
|  | LB_result->Angle[1] | B相电流相位角 | uint16_t | 1 | 2 | 39 | - | - | - | -
|  | LC_result->Angle[1] | C相电流相位角 | uint16_t | 1 | 2 | 40 | - | - | - | -
DEVICE_SET_PARAMETER | 保护数据 | Kr | 反时限过载脱扣等级 | uint8_t | 1 | 1 | 65 | 0 | 7 | 3 |  | 0:2级 1:3级 2:5级 3:10A级 4:10级 5:20级 6:30级 7:40级
|  | E_Kr | 反时限过载tE 脱扣等级 | uint8_t | 1 | 1 | 66 | 0 | 7 | 0 |  | 0:2级 1:3级 2:4级 3:5级 4:6级 5:8级 6:10级 7:12级
|  | protect_threshold[ZT_INVVERSE_OVERLOAD] | 反时限过载启动门限值 | uint16_t | 1 | 2 | 67 | 110 | 200 | 120 | %Ie | -
|  | overload_recov_en | 反时限过载自动复位 | uint8_t | 1 | 1 | 68 | 0 | 1 | 0 |  | 0：关闭 1：打开
|  | overload_cool_time | 反时限过载冷却时间 | uint8_t | 1 | 1 | 69 | 0 | 30 | 5 | min | -
|  | overload_startshield_time | 反时限过载起动屏蔽时间 | uint8_t | 1 | 1 | 71 | 0 | 30 | 1 | s | -
|  | protect_en[ZT_INVVERSE_OVERLOAD] | 反时限过载使能 | uint8_t | 1 | 1 | 72 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣门限值 | uint16_t | 1 | 2 | 73 | 100 | 800 | 200 | %Ie | -
|  | protect_delay[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣延时 | uint16_t | 10 | 2 | 74 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_CONSTANT_OVERLOAD] | 定时限过载使能 | uint8_t | 1 | 1 | 77 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_UNDERLOAD] | 欠载脱扣门限值 | uint16_t | 1 | 2 | 78 | 20 | 95 | 50 | %Ie | -
|  | protect_delay[ZT_UNDERLOAD] | 欠载脱扣延时 | uint16_t | 10 | 2 | 79 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_UNDERLOAD] | 欠载使能 | uint8_t | 1 | 1 | 82 | 0 | 3 | 0 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | short_start_protect | 短路启动脱扣值 | uint16_t | 1 | 2 | 83 | 200 | 1000 | 600 | %Ie | -
|  | protect_threshold[ZT_SHORT_CIRCUIT] | 短路运行脱扣值 | uint16_t | 1 | 2 | 84 | 200 | 800 | 300 | %Ie | -
|  | protect_delay[ZT_SHORT_CIRCUIT] | 短路脱扣延时 | uint16_t | 10 | 2 | 85 | 0.1 | 60 | 1 | s | -
|  | protect_en[ZT_SHORT_CIRCUIT] | 短路使能 | uint8_t | 1 | 1 | 89 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_LOCKEDROTOR] | 堵转脱扣门限值 | uint16_t | 1 | 2 | 90 | 150 | 700 | 300 | %Ie | -
|  | protect_delay[ZT_LOCKEDROTOR] | 堵转脱扣延时 | uint16_t | 10 | 2 | 91 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_LOCKEDROTOR] | 堵转使能 | uint8_t | 1 | 1 | 94 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_BLOCK] | 阻塞脱扣门限值 | uint16_t | 1 | 2 | 95 | 150 | 700 | 250 | %Ie | -
|  | protect_delay[ZT_BLOCK] | 阻塞脱扣延时 | uint16_t | 10 | 2 | 96 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_BLOCK] | 阻塞使能 | uint8_t | 1 | 1 | 99 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_delay[ZT_LACK] | 断相脱扣延时 | uint16_t | 10 | 2 | 100 | 0.1 | 30 | 1 | s | -
|  | lack_alarm_delay | 断相报警延时 | uint16_t | 10 | 2 | 101 | 0.1 | 30 | 0.1 | s | -
|  | protect_en[ZT_LACK] | 断相使能 | uint8_t | 1 | 1 | 102 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣门限值 | uint16_t | 1 | 2 | 103 | 10 | 80 | 30 | % | -
|  | protect_delay[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣延时 | uint16_t | 10 | 2 | 104 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_CURRENT_IMBALANCE] | 电流不平衡使能 | uint8_t | 1 | 1 | 107 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_OVERPOWER] | 过功率脱扣门限值 | uint16_t | 1 | 2 | 108 | 100 | 700 | 200 | %Pe | -
|  | protect_delay[ZT_OVERPOWER] | 过功率脱扣延时 | uint16_t | 10 | 2 | 109 | 1 | 600 | 5 | s | -
|  | protect_en[ZT_OVERPOWER] | 过功率使能 | uint8_t | 1 | 1 | 112 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_UNDERPOWER] | 欠功率脱扣门限值 | uint16_t | 1 | 2 | 113 | 5 | 100 | 50 | %Pe | -
|  | protect_delay[ZT_UNDERPOWER] | 欠功率脱扣延时 | uint16_t | 10 | 2 | 114 | 1 | 600 | 5 | s | -
|  | protect_en[ZT_UNDERPOWER] | 欠功率使能 | uint8_t | 1 | 1 | 117 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | ground_input_selection | 接地输入选择 | uint8_t | 1 | 1 | 118 | 0 | 2 | 0 |  | 0：电流矢量和 1：外接互感器1A 2：外接互感器15A | 2：原先5A修改成15A
|  | protect_threshold[ZT_GROUND] | 接地脱扣门限值 | uint16_t | 1 | 2 | 119 | 10 | 500 | 20 | %Ie | -
|  | protect_delay[ZT_GROUND] | 接地脱扣延时 | uint16_t | 10 | 2 | 120 | 0.1 | 60 | 5 | s | -
|  | ground_startshield_time | 接地起动屏蔽时间 | uint8_t | 10 | 1 | 123 | 0.1 | 120 | 0.1 | s | -
|  | ground_trip_type | 接地脱扣方式 | uint8_t | 1 | 1 | 124 | 0 | 1 | 1 |  | 0：接触器 1：断路器
|  | protect_en[ZT_GROUND] | 接地使能 | uint8_t | 1 | 1 | 125 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_LEAKAGE] | 漏电脱扣门限值 | uint16_t | 1 | 2 | 126 | 100 | 5000 | 300 | mA | -
|  | protect_delay[ZT_LEAKAGE] | 漏电脱扣延时 | uint16_t | 10 | 2 | 127 | 0.1 | 60 | 5 | s | -
|  | leakage_startshield_time | 漏电起动屏蔽时间 | uint16_t | 10 | 1 | 130 | 0.1 | 120 | 0.1 | s | -
|  | leakage_trip_type | 漏电脱扣方式 | uint8_t | 1 | 1 | 131 | 0 | 1 | 1 |  | 0：接触器 1：断路器
|  | protect_en[ZT_LEAKAGE] | 漏电使能 | uint8_t | 1 | 1 | 132 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_BREAK] | 溢出保护门限值 | uint16_t | 1 | 2 | 133 | 200 | 700 | 700 | %Ie | -
|  | protect_en[ZT_BREAK] | 溢出使能 | uint8_t | 1 | 1 | 134 | 0 | 3 | 1 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_delay[ZT_PHASE] | 相序脱扣延时 | uint16_t | 10 | 2 | 135 | 0.1 | 10 | 0.1 | s | -
|  | protect_en[ZT_PHASE] | 相序使能 | uint8_t | 1 | 1 | 137 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_OVERVOLTAGE] | 过电压脱扣门限值 | uint16_t | 1 | 2 | 138 | 110 | 150 | 120 | %Ue | -
|  | protect_delay[ZT_OVERVOLTAGE] | 过电压脱扣延时 | uint16_t | 10 | 2 | 139 | 0.1 | 60 | 0.1 | s | -
|  | protect_en[ZT_OVERVOLTAGE] | 过电压使能 | uint8_t | 1 | 1 | 142 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_UNDERVOLTAGE] | 欠电压脱扣门限值 | uint16_t | 1 | 2 | 143 | 50 | 90 | 85 | %Ue | -
|  | protect_delay[ZT_UNDERVOLTAGE] | 欠电压脱扣延时 | uint16_t | 10 | 2 | 144 | 0.1 | 60 | 0.1 | s | -
|  | protect_en[ZT_UNDERVOLTAGE] | 欠电压使能 | uint8_t | 1 | 1 | 147 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣门限值 | uint16_t | 1 | 2 | 148 | 10 | 40 | 15 | % | -
|  | protect_delay[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣延时 | uint16_t | 10 | 2 | 149 | 0.1 | 60 | 0.1 | s | -
|  | protect_en[ZT_VOLTAGE_IMBALANCE] | 电压不平衡使能 | uint8_t | 1 | 1 | 152 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_START_TIMEOUT] | 超时电流 | uint16_t | 1 | 2 | 153 | 100 | 150 | 110 | %Ie | -
|  | protect_delay[ZT_START_TIMEOUT] | 起动超时动作延时 | uint16_t | 10 | 2 | 154 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_START_TIMEOUT] | 起动超时使能 | uint8_t | 1 | 1 | 155 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_START_NUMBER] | 超时次数 | uint16_t | 1 | 2 | 156 | 1 | 10 | 3 |  | -
|  | protect_delay[ZT_START_NUMBER] | 时间范围 | uint16_t | 1 | 2 | 157 | 10 | 120 | 30 | min | -
|  | protect_en[ZT_START_NUMBER] | 超时次数使能 | uint8_t | 1 | 1 | 158 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_delay[ZT_EXTERNAL] | 外部故障脱扣延时 | uint16_t | 10 | 2 | 165 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_EXTERNAL] | 外部故障使能 | uint8_t | 1 | 1 | 167 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_RUN_TIMEOUT] | 运行超时报警时长 | uint16_t | 1 | 2 | 171 | 1000 | 20000 | 10000 | h | -
|  | protect_en[ZT_RUN_TIMEOUT] | 运行超时使能 | uint8_t | 1 | 1 | 172 | 0 | 3 | 2 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_FAIL_NUMBER] | 故障次数 | uint16_t | 1 | 2 | 173 | 10 | 1000 | 1000 | 次 | -
|  | protect_en[ZT_FAIL_NUMBER] | 故障次数使能 | uint8_t | 1 | 1 | 174 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | Kr_H | 反时限过载脱扣等级（高速） | uint8_t | 1 | 1 | 175 | 0 | 7 | 2 |  | 0:2级 1:3级 2:5级 3:10A级 4:10级 5:20级 6:30级 7:40级
|  | E_Kr_H | 反时限过载tE 脱扣等级（高速） | uint8_t | 1 | 1 | 176 | 0 | 7 | 0 |  | 0:2级 1:3级 2:4级 3:5级 4:6级 5:8级 6:10级 7:12级
|  | protect_threshold[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载启动门限值（高速） | uint16_t | 1 | 2 | 177 | 110 | 200 | 120 | %Ie | -
|  | overload_recov_en_hight | 反时限过载自动复位（高速） | uint8_t | 1 | 1 | 178 | 0 | 1 | 0 |  | 0：关闭 1：打开
|  | overload_cool_time_hight | 反时限过载冷却时间（高速） | uint8_t | 1 | 1 | 179 | 0 | 30 | 5 | min | -
|  | overload_startshield_time_hight | 反时限过载起动屏蔽时间（高速） | uint8_t | 1 | 1 | 181 | 0 | 30 | 1 | s | -
|  | protect_en[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载使能（高速） | uint8_t | 1 | 1 | 182 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣门限值（高速） | uint16_t | 1 | 2 | 183 | 100 | 800 | 200 | %Ie | -
|  | protect_delay[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣延时（高速） | uint16_t | 10 | 2 | 184 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载使能（高速） | uint8_t | 1 | 1 | 187 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_UNDERLOAD_HIGH] | 欠载脱扣门限值（高速） | uint16_t | 1 | 2 | 188 | 20 | 95 | 50 | %Ie | -
|  | protect_delay[ZT_UNDERLOAD_HIGH] | 欠载脱扣延时（高速） | uint16_t | 10 | 2 | 189 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_UNDERLOAD_HIGH] | 欠载使能（高速） | uint8_t | 1 | 1 | 192 | 0 | 3 | 0 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | short_start_protect_hight | 短路启动脱扣值（高速） | uint16_t | 1 | 2 | 193 | 200 | 1000 | 600 | %Ie | -
|  | protect_threshold[ZT_SHORT_CIRCUIT_HIGH] | 短路运行脱扣值（高速） | uint16_t | 1 | 2 | 194 | 200 | 800 | 300 | %Ie | -
|  | protect_delay[ZT_SHORT_CIRCUIT_HIGH] | 短路脱扣延时（高速） | uint16_t | 10 | 2 | 195 | 0.1 | 60 | 5 | s | -
|  | protect_en[ZT_SHORT_CIRCUIT_HIGH] | 短路使能（高速） | uint8_t | 1 | 1 | 199 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣门限值（高速） | uint16_t | 1 | 2 | 200 | 150 | 700 | 300 | %Ie | -
|  | protect_delay[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣延时（高速） | uint16_t | 10 | 2 | 201 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_LOCKEDROTOR_HIGH] | 堵转使能（高速） | uint8_t | 1 | 1 | 204 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_BLOCK_HIGH] | 阻塞脱扣门限值（高速） | uint16_t | 1 | 2 | 205 | 150 | 700 | 250 | %Ie | -
|  | protect_delay[ZT_BLOCK_HIGH] | 阻塞脱扣延时（高速） | uint16_t | 10 | 2 | 206 | 0.1 | 120 | 5 | s | -
|  | protect_en[ZT_BLOCK_HIGH] | 阻塞使能（高速） | uint8_t | 1 | 1 | 209 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_delay[ZT_LACK_HIGH] | 断相脱扣延时（高速） | uint16_t | 10 | 2 | 210 | 0.1 | 300 | 5 | s | -
|  | lack_alarm_delay_hight | 断相报警延时（高速） | uint16_t | 10 | 2 | 211 | 0.1 | 300 | 0.1 | s | -
|  | protect_en[ZT_LACK_HIGH] | 断相使能（高速） | uint8_t | 1 | 1 | 212 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣门限值（高速） | uint16_t | 1 | 2 | 213 | 10 | 80 | 30 | % | -
|  | protect_delay[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣延时（高速） | uint16_t | 10 | 2 | 214 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡使能（高速） | uint8_t | 1 | 1 | 217 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_OVERPOWER_HIGH] | 过功率脱扣门限值（高速） | uint16_t | 1 | 2 | 218 | 100 | 700 | 200 | %Pe | -
|  | protect_delay[ZT_OVERPOWER_HIGH] | 过功率脱扣延时（高速） | uint16_t | 10 | 2 | 219 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_OVERPOWER_HIGH] | 过功率使能（高速） | uint8_t | 1 | 1 | 222 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
|  | protect_threshold[ZT_UNDERPOWER_HIGH] | 欠功率脱扣门限值（高速） | uint16_t | 1 | 2 | 223 | 0 | 100 | 50 | %Pe | -
|  | protect_delay[ZT_UNDERPOWER_HIGH] | 欠功率脱扣延时（高速） | uint16_t | 10 | 2 | 224 | 0.1 | 600 | 5 | s | -
|  | protect_en[ZT_UNDERPOWER_HIGH] | 欠功率使能（高速） | uint8_t | 1 | 1 | 227 | 0 | 3 | 3 |  | 0：禁用 1：跳闸 2：报警 3：跳闸+报警
CONTROL_PARAMETER | 控制命令 | start1 | 起动1 | uint16_t | 1 | 2 | 244 |  |  |  |  | -
|  | start2 | 起动2 | uint16_t | 1 | 2 | 245 |  |  |  |  | -
|  | stop | 停机 | uint16_t | 1 | 2 | 247 |  |  |  |  | -
|  | reset | 复位 | uint16_t | 1 | 2 | 248 |  |  |  |  | -
|  | powerclear | 电量清零 | uint16_t | 1 | 2 | 249 |  |  |  |  | -
|  | eventclear | 事件总清 | uint16_t | 1 | 2 | 250 |  |  |  |  | -
|  | operationclear | 运行信息清零 | uint16_t | 1 | 2 | 251
|  | reset_run_timeout | 复位运行超时 | uint16_t | 1 | 2 | 252 |  |  |  |  | -
|  | reset_fault_number | 复位故障次数 | uint16_t | 1 | 2 | 253 |  |  |  |  | -
|  | flashclear | 恢复出厂 | uint16_t | 1 | 2 | 254
event_log | 保护事件 | fault_data | (上1次)故障原因 | uint8_t | 1 | 1 | 253 |  |  |  |  | 0: //正常 1：//反时限过载保护 2：//定时限过载保护 3：//欠载保护 4：//短路保护 5：//堵转保护 6：//阻塞保护 7：//缺相保护 8：//三相电流不平衡保护 9：//过功率保护 10：//欠功率保护 11：//接地保护 12：//漏电保护 13：//溢出保护 14：//相序保护 15：//过压保护 16：//欠压保护 17：//三相电压不平衡保护 18：//起动超时保护 19：//起动过频保护 20：//外部故障保护 21：//运行超时保护 22：//故障次数保护 23：//反时限过载保护（高速） 24：//定时限过载保护（高速） 25：//欠载保护（高速） 26：//短路保护（高速） 27：//堵转保护（高速） 28：//阻塞保护（高速） 29：//缺相保护（高速） 30：//三相电流不平衡保护（高速） 31：//过功率保护（高速） 32：//欠功率保护（高速） | 枚举量做了更新
|  | fault_phase | (上1次)故障相别 | uint8_t | 1 | 1 | 254 |  |  |  |  | -
|  | fault_time | (上1次)跳闸发生时刻 | uint8_t | 1 | 6 | 255 |  |  |  |  | -
|  | voltage_A | (上1次)跳闸前A相电压 | uint16_t | 10 | 2 | 256 |  |  |  |  | - | 原先为100 现改成10（防止数据溢出）
|  | voltage_B | (上1次)跳闸前B相电压 | uint16_t | 10 | 2 | 257 |  |  |  |  | -
|  | voltage_C | (上1次)跳闸前C相电压 | uint16_t | 10 | 2 | 258 |  |  |  |  | -
|  | current_A | (上1次)跳闸前A相电流 | float | 1 | 4 | 259 |  |  |  |  | -
|  | current_B | (上1次)跳闸前B相电流 | float | 1 | 4 | 260 |  |  |  |  | -
|  | current_C | (上1次)跳闸前C相电流 | float | 1 | 4 | 261 |  |  |  |  | -
|  | leakage | (上1次)跳闸前漏电电流 | float | 1 | 4 | 262 |  |  |  |  | -
|  | current_ground | (上1次)跳闸前接地电流 | float | 1 | 4 | 263 |  |  |  |  | -
|  | Active_Power | (上1次)跳闸前总有功率 | float | 1 | 4 | 264 |  |  |  |  | -
|  | ……………………………………… |  |  |  |  | 265 |  |  |  |  | -
|  | fault_data | (上10次)故障原因 | uint8_t | 1 | 1 | 266 |  |  |  |  | -
|  | fault_phase | (上10次)故障相别 | uint8_t | 1 | 1 | 267 |  |  |  |  | -
|  | fault_time | (上10次)跳闸发生时刻 | uint8_t | 1 | 6 | 268 |  |  |  |  | -
|  | voltage_A | (上10次)跳闸前A相电压 | uint16_t | 10 | 2 | 269 |  |  |  |  | - | 原先为100 现改成10（防止数据溢出）
|  | voltage_B | (上10次)跳闸前B相电压 | uint16_t | 10 | 2 | 270 |  |  |  |  | -
|  | voltage_C | (上10次)跳闸前C相电压 | uint16_t | 10 | 2 | 271 |  |  |  |  | -
|  | current_A | (上10次)跳闸前A相电流 | float | 1 | 4 | 272 |  |  |  |  | -
|  | current_B | (上10次)跳闸前B相电流 | float | 1 | 4 | 273 |  |  |  |  | -
|  | current_C | (上10次)跳闸前C相电流 | float | 1 | 4 | 274 |  |  |  |  | -
|  | leakage | (上10次)跳闸前漏电电流 | float | 1 | 4 | 275 |  |  |  |  | -
|  | current_ground | (上10次)跳闸前接地电流 | float | 1 | 4 | 276
|  | Active_Power | (上10次)跳闸前总有功率 | float | 1 | 4 | 277
| 告警事件 | state | (上1次)状态 | uint8_t | 1 | 1 | 278 |  |  |  |  | 0：停止 1：起动 2：起动（高速） 3：运行 4：运行（高速） 5：异常
|  | fault_data | (上1次)故障原因 | uint8_t | 1 | 1 | 279 |  |  |  |  | 同跳闸故障原因一样
|  | fault_phase | (上1次)故障相别 | uint8_t | 1 | 2 | 280
|  | fault_time | (上1次)告警发生时刻 | uint8_t | 1 | 6 | 281
|  | voltage_A | (上1次)告警前A相电压 | uint16_t | 10 | 2 | 282 | [5 empty] | 原先为100 现改成10（防止数据溢出）
|  | voltage_B | (上1次)告警前B相电压 | uint16_t | 10 | 2 | 283
|  | voltage_C | (上1次)告警前C相电压 | uint16_t | 10 | 2 | 284
|  | current_A | (上1次)告警前A相电流 | float | 1 | 4 | 285
|  | current_B | (上1次)告警前B相电流 | float | 1 | 4 | 286
|  | current_C | (上1次)告警前C相电流 | float | 1 | 4 | 287
|  | leakage | (上1次)告警前漏电电流 | float | 1 | 4 | 288
|  | current_ground | (上1次)告警前接地电流 | float | 1 | 4 | 289
|  | Active_Power | (上1次)告警前总有功率 | float | 1 | 4 | 290
|  | ……………………………………… |  |  |  |  | 291
|  | state | (上10次)状态 | uint8_t | 1 | 1 | 292
|  | fault_data | (上10次)故障原因 | uint8_t | 1 | 1 | 293
|  | fault_phase | (上10次)故障相别 | uint8_t | 1 | 2 | 294
|  | fault_time | (上10次)告警发生时刻 | uint8_t | 1 | 6 | 295
|  | voltage_A | (上10次)告警前A相电压 | uint16_t | 10 | 2 | 296 | [5 empty] | 原先为100 现改成10（防止数据溢出）
|  | voltage_B | (上10次)告警前B相电压 | uint16_t | 10 | 2 | 297
|  | voltage_C | (上10次)告警前C相电压 | uint16_t | 10 | 2 | 298
|  | current_A | (上10次)告警前A相电流 | float | 1 | 4 | 299
|  | current_B | (上10次)告警前B相电流 | float | 1 | 4 | 300
|  | current_C | (上10次)告警前C相电流 | float | 1 | 4 | 301
|  | leakage | (上10次)告警前漏电电流 | float | 1 | 4 | 302
|  | current_ground | (上10次)告警前接地电流 | float | 1 | 4 | 303
|  | Active_Power | (上10次)告警前总有功率 | float | 1 | 4 | 304
| 操作事件 | state | (上1次)状态 | uint8_t | 1 | 1 | 305
|  | operate_data | (上1次)操作方式 | uint8_t | 1 | 1 | 306 |  |  |  |  | 0：通用DI 1：起动1（本地） 2：起动2（本地） 3：停车（本地） 4：起动1（远程） 5：起动2（远程） 6：停车（远程） 7：起动1（通讯） 8：起动2（通讯） 9：停车（通讯） 10：复位（通讯） 11：复位（DI） 12：起动1（界面） 13：起动2（界面） 14：停车（界面） | 枚举量做了更新
|  | fault_time | (上1次)操作发生时刻 | uint8_t | 1 | 6 | 307
|  | ……………………………………… |  |  |  |  | 308
|  | state | (上10次)状态 | uint8_t | 1 | 1 | 309
|  | operate_data | (上10次)操作方式 | uint8_t | 1 | 1 | 310
|  | fault_time | (上10次)操作发生时刻 | uint8_t | 1 | 6 | 311
| DI事件 | state | (上1次)状态 | uint16_t | 1 | 1 | 312 |  |  |  |  | 0: 0变化1 1: 1变成0 | 新增DIDO事件
|  | channel | (上1次)通道 | uint16_t | 1 | 1 | 313
|  | fault_time | (上1次)发生时刻 | uint16_t | 1 | 6 | 314
|  | ……………………………………… |  |  |  |  | 315
|  | state | (上10次)状态 | uint16_t | 1 | 1 | 316
|  | channel | (上10次)通道 | uint16_t | 1 | 1 | 317
|  | fault_time | (上10次)发生时刻 | uint16_t | 1 | 6 | 318
| DO事件 | state | (上1次)状态 | uint16_t | 1 | 1 | 319 |  |  |  |  | 0: 0变化1 1: 1变成0
|  | channel | (上1次)通道 | uint16_t | 1 | 1 | 320
|  | fault_time | (上1次)发生时刻 | uint16_t | 1 | 6 | 321
|  | ……………………………………… |  |  |  |  | 322
|  | state | (上10次)状态 | uint16_t | 1 | 1 | 323
|  | channel | (上10次)通道 | uint16_t | 1 | 1 | 324
|  | fault_time | (上10次)发生时刻 | uint16_t | 1 | 6 | 325
SYSTEM_PARAMETER | 运行数据 | run_time_now | 本次运行时间 | uint32_t | 1 | 4 | 326
|  | stop_time_now | 本次停车时间 | uint32_t | 1 | 4 | 327
|  | run_time_all | 总运行时间 | uint32_t | 1 | 4 | 328
|  | stop_time_all | 总停车时间 | uint32_t | 1 | 4 | 329
|  | start_number | 起动次数 | uint32_t | 1 | 4 | 330
|  | trip_number | 脱扣次数 | uint32_t | 1 | 4 | 331
|  | start_current_max | 最大起动电流 | float | 100 | 4 | 332 | [5 empty] | 数据类型从uint32_t 变成 float
|  | run_current_max | 最大运行电流 | float | 100 | 4 | 333
| 系统参数 | work_mode | 工作模式 | uint8_t | 1 | 1 | 320 | 0 | 1 | 0 |  | 0：正常 1：调试模式1 虚拟电压和电流 2：调试模式2 虚拟电流
|  | rated_current_type | 额定电流规格 | uint16_t | 1 | 2 | 321 | 0 | 6 | 0 |  | 0：1A 1：5A 2：20A 3：40A 4：100A 5：300A 6：800A
|  | rated_current | 额定电流 | uint16_t | 10 | 2 | 322 | 0.5 | 2000 | 1 | A | 根据额定电流规格 显示不同范围和小数点
|  | rated_current_high | 额定电流（高速） | uint16_t | 10 | 2 | 323 | 0.5 | 2000 | 1 | A | 根据额定电流规格 显示不同范围和小数点
|  | rated_voltage_type | 额定电压规格 | uint16_t | 1 | 2 | 324 | 0 | 7 | 2 | V | 0: 220V 1: 240V 2: 380V 3: 400V 4: 415V 5: 440V 6: 660V 7: 690V
|  | rated_power | 额定功率 | float | 1 | 4 | 325 | 0.11 | 999 | 0,38 | KW | 根据额定电流*额定电压 显示不同范围和小数点
|  | rated_power_high | 额定功率（高速） | float | 1 | 4 | 326 | 0.11 | 999 | 0,38 | KW | 根据额定电流*额定电压 显示不同范围和小数点
|  | rated_freq | 额定频率 | uint8_t | 1 | 1 | 327 | 35 | 70 | 50 | HZ
|  | motor_type | 电机类型 | uint8_t | 1 | 1 | 328 | 0 | 3 | 0 |  | 0：普通电机 1：增安电机 2：双速电机 3：单相电机
|  | connection | 接线方式 | uint8_t | 1 | 1 | 329 | 0 | 2 | 1 |  | 0：三相三线 1：三相四线 2：单相二线
|  | ct_scale | CT变比 | uint8_t | 1 | 1 | 330 | 0 | 23 | 0 |  | 0：1 1：2.5 2: 5 3: 10 4: 15 5：20 6：30 7: 50 8: 75 9: 100 10: 150 11: 200 12: 250 13: 300 14: 400 15: 500 16: 600 17: 750 18: 800 19: 1000 20: 1200 21: 1500 22: 2000
|  | protect_selec | 保护选择 | uint8_t | 1 | 1 | 331 | 0 | 1 | 0 |  | 0：全波 1：基波
|  | language | 语言 | uint8_t | 1 | 1 | 332 | 0 | 1 | 0 |  | 0：中文 1：英文
|  | backlight | 背光 | uint8_t | 1 | 1 | 333 | 0 | 60 | 0 |  | 0为常亮
|  | setup | 液晶对比度 | uint8_t | 1 | 1 | 334 | 0 | 100 | 50 | %
|  | password | 液晶密码 | uint16_t | 1 | 2 | 335 | 0 | 9999 | 0
|  | timed_record_en | 启动方式（定时记录） | uint8_t | 1 | 1 | 336 | 0 | 2 | 2 |  | 0:总是记录 1：运行记录 2：禁用
|  | timed_record_mode | 记录模式（定时记录） | uint8_t | 1 | 1 | 337 | 0 | 1 | 1 |  | 0：记满停止 1：循环记录
|  | timed_record_time | 记录间隔（定时记录） | uint16_t | 1 | 2 | 338 | 1 | 600 | 1 | s
|  | modbus_addr[0] | 通讯modbus1地址 | uint8_t | 1 | 1 | 339 | 0 | 254 | 1
|  | modbus_baud[0] | 通讯modbus1波特率 | uint16_t | 1 | 2 | 340 | 0 | 6 | 0 |  | 0：9600 1：1200 2：2400 3：4800 4：9600 5：19200 6：115200
|  | modbus_check[0] | 通讯modbus1校验 | uint8_t | 1 | 1 | 341 | 0 | 3 | 0 |  | 0：even 1：none 2：odd 3：even
|  | modbus_addr[1] | 通讯modbus2地址 | uint8_t | 1 | 1 | 342 | 0 | 254 | 1
|  | modbus_baud[1] | 通讯modbus2波特率 | uint16_t | 1 | 2 | 343 | 0 | 6 | 0 |  | 0：9600 1：1200 2：2400 3：4800 4：9600 5：19200 6：115200
|  | modbus_check[1] | 通讯modbus2校验 | uint8_t | 1 | 1 | 344 | 0 | 3 | 0 |  | 0：even 1：none 2：odd 3：even
|  | can_addr | 通讯can地址 | uint8_t | 1 | 1 | 345 | 0 | 254 | 1
|  | can_baud | 通讯can波特率 | uint16_t | 1 | 2 | 346 | 0 | 3 | 0 |  | 0：125k 1：250k 2：500k 3：1000k
|  | can_check | 通讯can校验 | uint8_t | 1 | 1 | 347 | 0 | 2 | 0 |  | 0：even 1：none 2：odd
|  | transmit_type[0] | 变送器1设置类型 | uint8_t | 1 | 1 | 348 | 0 | 12 | 0 |  | 0:不使用 1：Ia 2：Ib 3：Ic 4：Iav 5：Uab 6：Ubc 7：Uca 8：Uav 9：PTC 10：热容量 11：P 12：F
|  | transmit_threshold[0] | 变送器1设置阈值 | uint16_t | 1 | 2 | 349 | 100 | 1000 | 200 | %
|  | transmit_type[1] | 变送器2设置类型 | uint8_t | 1 | 1 | 350 | 0 | 12 | 0 |  | 0:不使用 1：Ia 2：Ib 3：Ic 4：Iav 5：Uab 6：Ubc 7：Uca 8：Uav 9：PTC 10：热容量 11：P 12：F
|  | transmit_threshold[1] | 变送器2设置阈值 | uint16_t | 1 | 2 | 351 | 100 | 1000 | 200 | %
|  | transmit_type[2] | 变送器3设置类型 | uint8_t | 1 | 1 | 352 | 0 | 12 | 0 |  | 0:不使用 1：Ia 2：Ib 3：Ic 4：Iav 5：Uab 6：Ubc 7：Uca 8：Uav 9：PTC 10：热容量 11：P 12：F
|  | transmit_threshold[2] | 变送器3设置阈值 | uint16_t | 1 | 2 | 353 | 100 | 1000 | 200 | %
|  | transmit_type[3] | 变送器4设置类型 | uint8_t | 1 | 1 | 354 | 0 | 12 | 0 |  | 0:不使用 1：Ia 2：Ib 3：Ic 4：Iav 5：Uab 6：Ubc 7：Uca 8：Uav 9：PTC 10：热容量 11：P 12：F
|  | transmit_threshold[3] | 变送器4设置阈值 | uint16_t | 1 | 2 | 355 | 100 | 1000 | 200 | %
| 控制数据 | control_type | 控制权限 | uint8_t | 1 | 1 | 356 | 0 | 3 | 0 |  | 0: 全控 1：通讯 2: DI 3：面板 4：面板+DI 5:面板+通讯 6：DI+通讯
|  | control_start_type | 起动模式 | uint8_t | 1 | 1 | 357 | 0 | 4 | 0 |  | 0：简易模式 1：直接起动 2：双速模式 3：星三角 4：自耦降压 5：正反转
|  | voltage_start_type | 切换时序（降压启动） | uint8_t | 1 | 1 | 358 | 0 | 1 | 0 |  | 0: 先跳后合 1：先合后跳
|  | voltage_start1_delay | 起动1延时（降压启动） | uint16_t | 10 | 2 | 359 | 0.1 | 99 | 10 | s | -
|  | voltage_start_current | 切换电流（降压启动） | uint16_t | 10 | 2 | 360 | 0 | 3.5In | 0 |  | 0： 关闭 >0: 0.1In~3.5In
|  | way_start_type | 工作模式（双向启动） | uint8_t | 1 | 1 | 361 | 0 | 1 | 0 |  | 0: 手动操控 1：自动切换
|  | way_start_switch_delay | 切换延时（双向启动） | uint16_t | 1 | 1 | 362 | 1 | 99 | 5 | s | -
|  | way_start_corotation_delay | 正转延时（双向启动） | uint16_t | 1 | 1 | 363 | 1 | 600 | 30 | s | -
|  | way_start_reversal_delay | 反转延时（双向启动） | uint16_t | 1 | 1 | 364 | 1 | 600 | 30 | s | -
|  | speed_start_delay | 切换延时（双速启动） | uint16_t | 10 | 2 | 365 | 0.1 | 99 | 5 | s | -
|  | speed_start_current | 切换电流（双速启动） | uint16_t | 10 | 2 | 366 | 0 | 2 | 1.5 | In | 0： 关闭 >0: 0.3In~2In
|  | start_automatic_mode | 自起动模式 | uint8_t | 1 | 1 | 367 | 0 | 1 | 1 |  | 0：起动 1：恢复
|  | start_automatic_delay | 自起动延时 | uint16_t | 10 | 2 | 368 | 0.1 | 600 | 5 | s
|  | start_automatic_en | 自起动使能 | uint8_t | 1 | 1 | 369 | 0 | 1 | 0 |  | 0：关闭 1：打开
|  | loss_voltage_restore | 失压恢复电压 | uint8_t | 1 | 1 | 370 | 70 | 95 | 80 | %Ue
|  | loss_voltage_drop | 失压跌落电压 | uint8_t | 1 | 1 | 371 | 50 | 90 | 50 | %Ue
|  | loss_voltage_delay | 晃电时间 | uint8_t | 10 | 2 | 372 | 0 | 5 | 2 | s | 退出/0 0.1s~5.0s
|  | loss_voltage_allow_delay | 失压允许时间 | uint16_t | 10 | 2 | 373 | 0.5 | 99 | 5
|  | loss_voltage_restart_delay | 失压重启延时 | uint16_t | 10 | 2 | 374 | 0.1 | 60 | 0.2 | s
|  | loss_voltage_restart_en | 失压重启使能 | uint8_t | 1 | 1 | 375 | 0 | 1 | 0 |  | 0：关闭 1：打开
|  | DI_type[0] | DI1类型 | uint8_t | 1 | 1 | 376 | 0 | 1 | 0 |  | 0：常开 1：常闭
|  | DI_mode[0] | DI1定义 | uint8_t | 1 | 1 | 377 | 0 | 10 | 1 |  | 0：通用DI 1：就地/远方 2：启动1（就地） 3：启动1（远方） 4：启动2（就地） 5：启动2（远方） 6：停车（就地） 7：停车（远方） 8：复位 9：紧急停车 10：KM1状态 11：KM2状态 12：QF状态 13：外部故障 14：未定义 | 枚举量做了更新
|  | DI_type[1] | DI2类型 | uint8_t | 1 | 1 | 378 | 0 | 1 | 0 |  | 0：常开 1：常闭
|  | DI_mode[1] | DI2定义 | uint8_t | 1 | 1 | 379 | 0 | 10 | 2 |  | 0：通用DI 1：就地/远方 2：启动1（就地） 3：启动1（远方） 4：启动2（就地） 5：启动2（远方） 6：停车（就地） 7：停车（远方） 8：复位 9：紧急停车 10：KM1状态 11：KM2状态 12：QF状态 13：外部故障 14：未定义 | 枚举量做了更新
|  | DI_type[2] | DI3类型 | uint8_t | 1 | 1 | 380 | 0 | 1 | 0 |  | 0：常开 1：常闭
|  | DI_mode[2] | DI3定义 | uint8_t | 1 | 1 | 381 | 0 | 10 | 3 |  | 0：通用DI 1：就地/远方 2：启动1（就地） 3：启动1（远方） 4：启动2（就地） 5：启动2（远方） 6：停车（就地） 7：停车（远方） 8：复位 9：紧急停车 10：KM1状态 11：KM2状态 12：QF状态 13：外部故障 14：未定义 | 枚举量做了更新
|  | DI_type[3] | DI4类型 | uint8_t | 1 | 1 | 382 | 0 | 1 | 0 |  | 0：常开 1：常闭
|  | DI_mode[3] | DI4定义 | uint8_t | 1 | 1 | 383 | 0 | 10 | 4 |  | 0：通用DI 1：就地/远方 2：启动1（就地） 3：启动1（远方） 4：启动2（就地） 5：启动2（远方） 6：停车（就地） 7：停车（远方） 8：复位 9：紧急停车 10：KM1状态 11：KM2状态 12：QF状态 13：外部故障 14：未定义 | 枚举量做了更新
|  | DI_type[4] | DI5类型 | uint8_t | 1 | 1 | 384 | 0 | 1 | 0 |  | 0：常开 1：常闭
|  | DI_mode[4] | DI5定义 | uint8_t | 1 | 1 | 385 | 0 | 10 | 10 |  | 0：通用DI 1：就地/远方 2：启动1（就地） 3：启动1（远方） 4：启动2（就地） 5：启动2（远方） 6：停车（就地） 7：停车（远方） 8：复位 9：紧急停车 10：KM1状态 11：KM2状态 12：QF状态 13：外部故障 14：未定义 | 枚举量做了更新
|  | DI_type[5] | DI6类型 | uint8_t | 1 | 1 | 386 | 0 | 1 | 0 |  | 0：常开 1：常闭
|  | DI_mode[5] | DI6定义 | uint8_t | 1 | 1 | 387 | 0 | 10 | 0 |  | 0：通用DI 1：就地/远方 2：启动1（就地） 3：启动1（远方） 4：启动2（就地） 5：启动2（远方） 6：停车（就地） 7：停车（远方） 8：复位 9：紧急停车 10：KM1状态 11：KM2状态 12：QF状态 13：外部故障 14：未定义 | 枚举量做了更新
|  | DO_mode[0] | DO1定义 | uint8_t | 1 | 1 | 389 | 0 | 11 | 1 |  | 0：不投用 1：起动1 2：起动2 3：起动3 4：脱扣出口（断接触器） 5：断路器 6：报警故障输出 7：脱扣故障输出 8：起动状态输出 9：运行状态输出 10：联动出口1 11：联动出口2 | 枚举量做了更新
|  | DO_delay[0] | DO1脉冲时间 | uint16_t | 10 | 2 | 390 | 0 | 25 | 0.3 | s | 0：保持 0.1s~25s
|  | DO_mode[1] | DO2定义 | uint8_t | 1 | 1 | 392 | 4 | 11 | 2 |  | 4：脱扣出口（断接触器） 5：断路器 6：报警故障输出 7：脱扣故障输出 8：起动状态输出 9：运行状态输出 10：联动出口1 11：联动出口2 | 枚举量做了更新
|  | DO_delay[1] | DO2脉冲时间 | uint16_t | 10 | 2 | 393 | 0 | 25 | 0.3 | s | 0：保持 0.1s~25s
|  | DO_mode[2] | DO3定义 | uint8_t | 1 | 1 | 395 | 0 | 11 | 3 |  | 0：不投用 1：起动1 2：起动2 3：起动3 4：脱扣出口（断接触器） 5：断路器 6：报警故障输出 7：脱扣故障输出 8：起动状态输出 9：运行状态输出 10：联动出口1 11：联动出口2 | 枚举量做了更新
|  | DO_delay[2] | DO3脉冲时间 | uint16_t | 10 | 2 | 396 | 0 | 25 | 0.3 | s | 0：保持 0.1s~25s
|  | DO_mode[3] | DO4定义 | uint8_t | 1 | 1 | 398 | 0 | 11 | 4 |  | 0：不投用 1：起动1 2：起动2 3：起动3 4：脱扣出口（断接触器） 5：断路器 6：报警故障输出 7：脱扣故障输出 8：起动状态输出 9：运行状态输出 10：联动出口1 11：联动出口2 | 枚举量做了更新
|  | DO_delay[3] | DO4脉冲时间 | uint16_t | 10 | 2 | 399 | 0 | 25 | 0.3 | s | 0：保持 0.1s~25s
| 调试数据 | debug_mode_DI | DI模拟配置 | uint8_t | 1 | 1 | 400 | 0 | 1 | 0 |  | 0：真实值 1：模拟值
|  | DI_state_simulate[0] | 模拟DI1 | uint8_t | 1 | 1 | 401 | 0 | 1 | 0 |  | 0：断开 1：闭合
|  | DI_state_simulate[1] | 模拟DI2 | uint8_t | 1 | 1 | 402 | 0 | 1 | 0 |  | 0：断开 1：闭合
|  | DI_state_simulate[2] | 模拟DI3 | uint8_t | 1 | 1 | 403 | 0 | 1 | 0 |  | 0：断开 1：闭合
|  | DI_state_simulate[3] | 模拟DI4 | uint8_t | 1 | 1 | 404 | 0 | 1 | 0 |  | 0：断开 1：闭合
|  | DI_state_simulate[4] | 模拟DI5 | uint8_t | 1 | 1 | 405 | 0 | 1 | 0 |  | 0：断开 1：闭合
|  | DI_state_simulate[5] | 模拟DI6 | uint8_t | 1 | 1 | 406 | 0 | 1 | 0 |  | 0：断开 1：闭合
|  | debug_mode_DO | DO模拟配置 | uint8_t | 1 | 1 | 407 | 0 | 1 | 0 |  | 0：真实值 1：模拟值
|  | DO_state_simulate[0] | 模拟DO1 | uint8_t | 1 | 1 | 408 | 0 | 1 | 0 |  | 0：不动作 1：动作
|  | DO_state_simulate[1] | 模拟DO2 | uint8_t | 1 | 1 | 409 | 0 | 1 | 0 |  | 0：不动作 1：动作
|  | DO_state_simulate[2] | 模拟DO3 | uint8_t | 1 | 1 | 410 | 0 | 1 | 0 |  | 0：不动作 1：动作
|  | DO_state_simulate[3] | 模拟DO4 | uint8_t | 1 | 1 | 411 | 0 | 1 | 0 |  | 0：不动作 1：动作
|  | Power_Fac_simulate | 模拟功率因素 | float | 1 | 4 | 412 | -1 | 1 | 1
|  | Current_simulate_A | 模拟A相电流 | uint16_t | 1 | 2 | 413 | 0 | 1100 | 100 | %Ie | 仅调试模式有效； 1-200；步进1； 200-1100；步进10
|  | Current_simulate_B | 模拟B相电流 | uint16_t | 1 | 2 | 414 | 0 | 1100 | 100 | %Ie
|  | Current_simulate_C | 模拟C相电流 | uint16_t | 1 | 2 | 415 | 0 | 1100 | 100 | %Ie
|  | Total_Creepage_simulate | 模拟漏电流 | uint16_t | 1 | 2 | 416 | 0 | 1100 | 100 | %Ie
|  | Current_Ground_simulate | 模拟接地电流 | uint16_t | 1 | 2 | 417 | 0 | 1100 | 100 | %Ie
|  | Voltage_simulate_A | 模拟A相电压 | uint16_t | 1 | 2 | 418 | 0 | 160 | 100 | %Ue | 仅调试模式有效； 1-160；步进1
|  | Voltage_simulate_B | 模拟B相电压 | uint16_t | 1 | 2 | 419 | 0 | 160 | 100 | %Ue
|  | Voltage_simulate_C | 模拟C相电压 | uint16_t | 1 | 2 | 420 | 0 | 160 | 100 | %Ue
MANUFACTURER_PARAMETER | 厂内参数 | rated_current_type | 额定电流规格 | uint16_t | 1 | 2 | 421 | 0 | 6 | 0 |  | 0：1A 1：5A 2：20A 3：40A 4：100A 5：300A 6：800A
|  | main_type | 主型选择 | uint8_t | 1 | 1 | 422 | 0 | 0 | 0 |  | 0:基础版
|  | voltage_type | 电压选型 | uint8_t | 1 | 1 | 423 | 0 | 1 | 0 |  | 0：常规电压 1：特殊电压
|  | leakage_ct | 漏电变比 | uint8_t | 1 | 1 | 424 | 0 | 2 | 0 |  | 0: 无 1: 1A 2: 15A
|  | meter_mode | 校表模式 | uint8_t | 1 | 1 | 425
|  | anti_shock_mode | 抗晃电模式 | uint8_t | 1 | 1 | 426 | 0 | 1 | 0 |  | 0: 普通 1：增强
|  | extension_mode | 扩展模式 | uint8_t | 1 | 1 | 427
| 校表参数 | 校表流程：1.先写入校表参数 2.启动校表 3.电流偏置 4.校表1 5.校表2 6.校表其他电流 7.结束校表 | [10 empty] | （还在和设备讨论中）
|  | device.check_curgain | 电流增益（输入电流值） | 0xF002 | float | 4
|  | device.check_curgain2 | 第二段电流增益（输入电流值） | 0xF004 | float | 4
|  | device.check_curgain4 | 其他电流增益 | 0xF006 | float | 4
|  | device.check_volgain | 电压增益（输入电压值） | 0xF008 | float | 4
|  | device.check_powergain | 功率增益（输入功率值） | 0xF00A | float | 4
|  | device.check_powerfac | 功率增益（功率因素） | 0xF00C | float | 4
|  | bool caliStart(void) | 启动校表 | 0xF000 | uint16_t | 2
|  | bool caliCurOffset(void) | 电流偏置 | 0xF001 | uint16_t | 2
|  | start_meter1 | 校表1 | 0xF00F | uint16_t | 2
|  | start_meter2 | 校表2 | 0xF010 | uint16_t | 2
|  | start_othercurrent | 校表其他电流 | 0xF011 | uint16_t | 2
|  | bool caliStop(void) | 结束校准 | 0xF012 | uint16_t | 2
|  | get_time | 获取时间 | 0xF100 | uint16_t | 8 | 空 空 年 月 日 时 分 秒

## Modbus对象字典
结构体名 | 描述 | 变量名 | 变量描述 | 寄存器地址 | 数据类型 | 数据长度 | 读写权限
POWER_PARAMETER | 测量数据 | Total_AB_Voltage | AB线电压 | 0x1000 | uint16_t | 2 | readonly
|  | Total_BC_Voltage | BC线电压 | 0x1001 | uint16_t | 2 | readonly
|  | Total_AC_Voltage | CA线电压 | 0x1002 | uint16_t | 2 | readonly
|  | LA_result->Voltage | A相电压 | 0x1003 | uint16_t | 2 | readonly
|  | LB_result->Voltage | B相电压 | 0x1004 | uint16_t | 2 | readonly
|  | LC_result->Voltage | C相电压 | 0x1005 | uint16_t | 2 | readonly
|  | Voltage_N | N相电压 | 0x1006 | uint16_t | 2 | readonly
|  | LA_result->Current | A相电流 | 0x1007 | float | 4 | readonly
|  | LB_result->Current | B相电流 | 0x1009 | float | 4 | readonly
|  | LC_result->Current | C相电流 | 0x100B | float | 4 | readonly
|  | Total_Creepage | 漏电流 | 0x100D | float | 4 | readonly
|  | Current_Ground | 接地电流 | 0x100F | float | 4 | readonly
|  | Total_Electric_Quantity | 总电量 | 0x1011 | float | 4 | readonly
|  | LA_result->Active_Energy | A有功电量 | 0x1013 | float | 4 | readonly
|  | LB_result->Active_Energy | B有功电量 | 0x1015 | float | 4 | readonly
|  | LC_result->Active_Energy | C有功电量 | 0x1017 | float | 4 | readonly
|  | LA_result->Reactive_Energy | A无功电量 | 0x1019 | float | 4 | readonly
|  | LB_result->Reactive_Energy | B无功电量 | 0x101B | float | 4 | readonly
|  | LC_result->Reactive_Energy | C无功电量 | 0x101D | float | 4 | readonly
|  | Total_Active_Power[4] | 总有功功率 | 0x101F | float | 4 | readonly
|  | LA_result->Active_Power[4] | A相有功功率 | 0x1021 | float | 4 | readonly
|  | LB_result->Active_Power[4] | B相有功功率 | 0x1023 | float | 4 | readonly
|  | LC_result->Active_Power[4] | C相有功功率 | 0x1025 | float | 4 | readonly
|  | Total_Reactive_Power[4] | 总无功功率 | 0x1027 | float | 4 | readonly
|  | LA_result->Reactive_Power[4] | A相无功功率 | 0x1029 | float | 4 | readonly
|  | LB_result->Reactive_Power[4] | B相无功功率 | 0x102B | float | 4 | readonly
|  | LC_result->Reactive_Power[4] | C相无功功率 | 0x102D | float | 4 | readonly
|  | Total_Apparent_Power[4] | 总视在功率 | 0x102F | float | 4 | readonly
|  | LA_result->Apparent_Power[4] | A相视在功率 | 0x1031 | float | 4 | readonly
|  | LB_result->Apparent_Power[4] | B相视在功率 | 0x1033 | float | 4 | readonly
|  | LC_result->Apparent_Power[4] | C相视在功率 | 0x1035 | float | 4 | readonly
|  | Total_Power_Factor | 总功率因数 | 0x1037 | float | 1 | readonly
|  | LA_result->Power_Factor | A相功率因数 | 0x1039 | float | 1 | readonly
|  | LB_result->Power_Factor | B相功率因数 | 0x103B | float | 1 | readonly
|  | LC_result->Power_Factor | C相功率因数 | 0x103D | float | 1 | readonly
|  | LA_result->Angle[0] | A相相位角 | 0x103F | uint16_t | 2 | readonly
|  | LB_result->Angle[0] | B相相位角 | 0x1040 | uint16_t | 2 | readonly
|  | LC_result->Angle[0] | C相相位角 | 0x1041 | uint16_t | 2 | readonly
|  | LA_result->Voltage_wave | 基波A相电压 | 0x1042 | uint16_t | 2 | readonly
|  | LB_result->Voltage_wave | 基波B相电压 | 0x1043 | uint16_t | 2 | readonly
|  | LC_result->Voltage_wave | 基波C相电压 | 0x1044 | uint16_t | 2 | readonly
|  | LA_result->Current_wave | 基波A相电流 | 0x1045 | float | 4 | readonly
|  | LB_result->Current_wave | 基波B相电流 | 0x1047 | float | 4 | readonly
|  | LC_result->Current_wave | 基波C相电流 | 0x1049 | float | 4 | readonly
|  | DI_state[0] | DI0状态 | 0x104B | uint16_t | 2 | readonly
|  | DI_state[1] | DI1状态 | 0x104C | uint16_t | 2 | readonly
|  | DI_state[2] | DI2状态 | 0x104D | uint16_t | 2 | readonly
|  | DI_state[3] | DI3状态 | 0x104E | uint16_t | 2 | readonly
|  | DI_state[4] | DI4状态 | 0x104F | uint16_t | 2 | readonly
|  | DI_state[5] | DI5状态 | 0x1050 | uint16_t | 2 | readonly
|  | DO_state[0] | DO0状态 | 0x1051 | uint16_t | 2 | readonly
|  | DO_state[1] | DO1状态 | 0x1052 | uint16_t | 2 | readonly
|  | DO_state[2] | DO2状态 | 0x1053 | uint16_t | 2 | readonly
|  | DO_state[3] | DO3状态 | 0x1054 | uint16_t | 2 | readonly
|  | LA_result->harmonic_voltage | A相电压谐波 | 0x1055 | uint16_t | 2 | readonly
|  | LB_result->harmonic_voltage | B相电压谐波 | 0x1056 | uint16_t | 2 | readonly
|  | LC_result->harmonic_voltage | C相电压谐波 | 0x1057 | uint16_t | 2 | readonly
|  | LA_result->harmonic_current | A相电流谐波 | 0x1058 | uint16_t | 2 | readonly
|  | LB_result->harmonic_current | B相电流谐波 | 0x1059 | uint16_t | 2 | readonly
|  | LC_result->harmonic_current | C相电流谐波 | 0x105A | uint16_t | 2 | readonly
|  | LA_result->harmonic_power | A相功率谐波 | 0x105B | uint16_t | 2 | readonly
|  | LB_result->harmonic_power | B相功率谐波 | 0x105C | uint16_t | 2 | readonly
|  | LC_result->harmonic_power | C相功率谐波 | 0x105D | uint16_t | 2 | readonly
|  | LA_result->Angle[1] | A相电流相位角 | 0x105E | uint16_t | 2 | readonly
|  | LB_result->Angle[1] | B相电流相位角 | 0x105F | uint16_t | 2 | readonly
|  | LC_result->Angle[1] | C相电流相位角 | 0x1060 | uint16_t | 2 | readonly
DEVICE_SET_PARAMETER | 保护数据 | Kr | 反时限过载脱扣等级 | 0x3000 | uint8_t | 1 | readwrite
|  | E_Kr | 反时限过载tE 脱扣等级 | 0x3001 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_INVVERSE_OVERLOAD] | 反时限过载启动门限值 | 0x3002 | uint16_t | 2 | readwrite
|  | overload_recov_en | 反时限过载自动复位 | 0x3003 | uint8_t | 1 | readwrite
|  | overload_cool_time | 反时限过载冷却时间 | 0x3004 | uint8_t | 1 | readwrite
|  | overload_startshield_time | 反时限过载起动屏蔽时间 | 0x3005 | uint8_t | 1 | readwrite
|  | protect_en[ZT_INVVERSE_OVERLOAD] | 反时限过载脱扣使能 | 0x3006 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣门限值 | 0x3007 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣延时 | 0x3008 | uint16_t | 2 | readwrite
|  | protect_en[ZT_CONSTANT_OVERLOAD] | 定时限过载脱扣使能 | 0x3009 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_UNDERLOAD] | 欠载脱扣门限值 | 0x301A | uint16_t | 2 | readwrite
|  | protect_delay[ZT_UNDERLOAD] | 欠载脱扣延时 | 0x301B | uint16_t | 2 | readwrite
|  | protect_en[ZT_UNDERLOAD] | 欠载脱扣使能 | 0x301C | uint8_t | 1 | readwrite
|  | short_start_protect | 短路启动脱扣值 | 0x301D | uint16_t | 2 | readwrite
|  | protect_threshold[ZT_SHORT_CIRCUIT] | 短路运行脱扣值 | 0x301E | uint16_t | 2 | readwrite
|  | protect_delay[ZT_SHORT_CIRCUIT] | 短路脱扣延时 | 0x301F | uint16_t | 2 | readwrite
|  | protect_en[ZT_SHORT_CIRCUIT] | 短路脱扣使能 | 0x3020 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_LOCKEDROTOR] | 堵转脱扣门限值 | 0x3021 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_LOCKEDROTOR] | 堵转脱扣延时 | 0x3022 | uint16_t | 2 | readwrite
|  | protect_en[ZT_LOCKEDROTOR] | 堵转脱扣使能 | 0x3023 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_BLOCK] | 阻塞脱扣门限值 | 0x3024 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_BLOCK] | 阻塞脱扣延时 | 0x3025 | uint16_t | 2 | readwrite
|  | protect_en[ZT_BLOCK] | 阻塞脱扣使能 | 0x3026 | uint8_t | 1 | readwrite
|  | protect_delay[ZT_LACK] | 断相脱扣延时 | 0x3027 | uint16_t | 2 | readwrite
|  | lack_alarm_delay | 断相告警延时 | 0x3028 | uint16_t | 2 | readwrite
|  | protect_en[ZT_LACK] | 断相脱扣使能 | 0x3029 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣门限值 | 0x302A | uint16_t | 2 | readwrite
|  | protect_delay[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣延时 | 0x302B | uint16_t | 2 | readwrite
|  | protect_en[ZT_CURRENT_IMBALANCE] | 电流不平衡脱扣使能 | 0x302C | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_OVERPOWER] | 过功率脱扣门限值 | 0x302D | uint16_t | 2 | readwrite
|  | protect_delay[ZT_OVERPOWER] | 过功率脱扣延时 | 0x302E | uint16_t | 2 | readwrite
|  | protect_en[ZT_OVERPOWER] | 过功率脱扣使能 | 0x302F | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_UNDERPOWER] | 欠功率脱扣门限值 | 0x3030 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_UNDERPOWER] | 欠功率脱扣延时 | 0x3031 | uint16_t | 2 | readwrite
|  | protect_en[ZT_UNDERPOWER] | 欠功率脱扣使能 | 0x3032 | uint8_t | 1 | readwrite
|  | ground_input_selection | 接地输入选择 | 0x3033 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_GROUND] | 接地脱扣门限值 | 0x3034 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_GROUND] | 接地脱扣延时 | 0x3035 | uint16_t | 2 | readwrite
|  | ground_startshield_time | 接地起动屏蔽时间 | 0x3036 | uint16_t | 1 | readwrite
|  | ground_trip_type | 接地脱扣方式 | 0x3037 | uint8_t | 1 | readwrite
|  | protect_en[ZT_GROUND] | 接地脱扣使能 | 0x3038 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_LEAKAGE] | 漏电脱扣门限值 | 0x3039 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_LEAKAGE] | 漏电脱扣延时 | 0x303A | uint16_t | 2 | readwrite
|  | leakage_startshield_time | 漏电起动屏蔽时间 | 0x303B | uint16_t | 1 | readwrite
|  | leakage_trip_type | 漏电脱扣方式 | 0x303C | uint8_t | 1 | readwrite
|  | protect_en[ZT_LEAKAGE] | 漏电脱扣使能 | 0x303D | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_BREAK] | 溢出保护门限值 | 0x303E | uint16_t | 2 | readwrite
|  | protect_en[ZT_BREAK] | 溢出脱扣使能 | 0x303F | uint8_t | 1 | readwrite
|  | protect_delay[ZT_PHASE] | 相序脱扣延时 | 0x3040 | uint16_t | 2 | readwrite
|  | protect_en[ZT_PHASE] | 相序脱扣使能 | 0x3041 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_OVERVOLTAGE] | 过电压脱扣门限值 | 0x3042 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_OVERVOLTAGE] | 过电压脱扣延时 | 0x3043 | uint16_t | 2 | readwrite
|  | protect_en[ZT_OVERVOLTAGE] | 过电压脱扣使能 | 0x3044 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_UNDERVOLTAGE] | 欠电压脱扣门限值 | 0x3045 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_UNDERVOLTAGE] | 欠电压脱扣延时 | 0x3046 | uint16_t | 2 | readwrite
|  | protect_en[ZT_UNDERVOLTAGE] | 欠电压脱扣使能 | 0x3047 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣门限值 | 0x3048 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣延时 | 0x3049 | uint16_t | 2 | readwrite
|  | protect_en[ZT_VOLTAGE_IMBALANCE] | 电压不平衡脱扣使能 | 0x304A | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_START_TIMEOUT] | 超时电流 | 0x304B | uint8_t | 2 | readwrite
|  | protect_delay[ZT_START_TIMEOUT] | 起动超时动作延时 | 0x304C | uint16_t | 2 | readwrite
|  | protect_en[ZT_START_TIMEOUT] | 起动超时脱扣使能 | 0x304D | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_START_NUMBER] | 超时次数 | 0x304E | uint8_t | 2 | readwrite
|  | protect_delay[ZT_START_NUMBER] | 时间范围 | 0x304F | uint16_t | 2 | readwrite
|  | protect_en[ZT_START_NUMBER] | 超时次数脱扣使能 | 0x3050 | uint8_t | 1 | readwrite
|  | protect_delay[ZT_EXTERNAL] | 外部故障脱扣延时 | 0x3051 | uint16_t | 2 | readwrite
|  | protect_en[ZT_EXTERNAL] | 外部故障脱扣使能 | 0x3052 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_RUN_TIMEOUT] | 运行超时报警时长 | 0x3053 | uint16_t | 2 | readwrite
|  | protect_en[ZT_RUN_TIMEOUT] | 运行超时脱扣使能 | 0x3054 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_FAIL_NUMBER] | 故障次数 | 0x3055 | uint16_t | 2 | readwrite
|  | protect_en[ZT_FAIL_NUMBER] | 故障次数报警使能 | 0x3056 | uint8_t | 1 | readwrite
|  | Kr_H | 反时限过载脱扣等级（高速） | 0x3500 | uint8_t | 1 | readwrite
|  | E_Kr_H | 反时限过载tE 脱扣等级（高速） | 0x3501 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载启动门限值（高速） | 0x3502 | uint16_t | 2 | readwrite
|  | overload_recov_en_hight | 反时限过载自动复位（高速） | 0x3503 | uint8_t | 1 | readwrite
|  | overload_cool_time_hight | 反时限过载冷却时间（高速） | 0x3504 | uint8_t | 1 | readwrite
|  | overload_startshield_time_hight | 反时限过载起动屏蔽时间（高速） | 0x3505 | uint8_t | 1 | readwrite
|  | protect_en[ZT_INVVERSE_OVERLOAD_HIGH] | 反时限过载脱扣使能（高速） | 0x3506 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣门限值（高速） | 0x3507 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣延时（高速） | 0x3508 | uint16_t | 2 | readwrite
|  | protect_en[ZT_CONSTANT_OVERLOAD_HIGH] | 定时限过载脱扣使能（高速） | 0x3509 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_UNDERLOAD_HIGH] | 欠载脱扣门限值（高速） | 0x350A | uint16_t | 2 | readwrite
|  | protect_delay[ZT_UNDERLOAD_HIGH] | 欠载脱扣延时（高速） | 0x350B | uint16_t | 2 | readwrite
|  | protect_en[ZT_UNDERLOAD_HIGH] | 欠载脱扣使能（高速） | 0x350C | uint8_t | 1 | readwrite
|  | short_start_protect_hight | 短路启动脱扣值（高速） | 0x350D | uint16_t | 2 | readwrite
|  | protect_threshold[ZT_SHORT_CIRCUIT_HIGH] | 短路运行脱扣值（高速） | 0x350E | uint16_t | 2 | readwrite
|  | protect_delay[ZT_SHORT_CIRCUIT_HIGH] | 短路脱扣延时（高速） | 0x350F | uint16_t | 2 | readwrite
|  | protect_en[ZT_SHORT_CIRCUIT_HIGH] | 短路脱扣使能（高速） | 0x3510 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣门限值（高速） | 0x3511 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣延时（高速） | 0x3512 | uint16_t | 2 | readwrite
|  | protect_en[ZT_LOCKEDROTOR_HIGH] | 堵转脱扣使能（高速） | 0x3513 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_BLOCK_HIGH] | 阻塞脱扣门限值（高速） | 0x3514 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_BLOCK_HIGH] | 阻塞脱扣延时（高速） | 0x3515 | uint16_t | 2 | readwrite
|  | protect_en[ZT_BLOCK_HIGH] | 阻塞脱扣使能（高速） | 0x3516 | uint8_t | 1 | readwrite
|  | protect_delay[ZT_LACK_HIGH] | 断相脱扣延时（高速） | 0x3517 | uint16_t | 2 | readwrite
|  | lack_high_alarm_delay | 断相报警延时（高速） | 0x3518 | uint16_t | 2 | readwrite
|  | protect_en[ZT_LACK_HIGH] | 断相脱扣使能（高速） | 0x3519 | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣门限值（高速） | 0x351A | uint16_t | 2 | readwrite
|  | protect_delay[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣延时（高速） | 0x351B | uint16_t | 2 | readwrite
|  | protect_en[ZT_CURRENT_IMBALANCE_HIGH] | 电流不平衡脱扣使能（高速） | 0x351C | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_OVERPOWER_HIGH] | 过功率脱扣门限值（高速） | 0x351D | uint16_t | 2 | readwrite
|  | protect_delay[ZT_OVERPOWER_HIGH] | 过功率脱扣延时（高速） | 0x351E | uint16_t | 2 | readwrite
|  | protect_en[ZT_OVERPOWER_HIGH] | 过功率脱扣使能（高速） | 0x351F | uint8_t | 1 | readwrite
|  | protect_threshold[ZT_UNDERPOWER_HIGH] | 欠功率脱扣门限值（高速） | 0x3520 | uint16_t | 2 | readwrite
|  | protect_delay[ZT_UNDERPOWER_HIGH] | 欠功率脱扣延时（高速） | 0x3521 | uint16_t | 2 | readwrite
|  | protect_en[ZT_UNDERPOWER_HIGH] | 欠功率脱扣使能（高速） | 0x3522 | uint8_t | 1 | readwrite
CONTROL_PARAMETER | 控制命令 | start1 | 起动1 | 0x8000 | uint8_t | 1 | writeonly
|  | start2 | 起动2 | 0x8001 | uint8_t | 1 | writeonly
|  | stop | 停机 | 0x8002 | uint8_t | 1 | writeonly
|  | reset | 复位 | 0x8003 | uint8_t | 1 | writeonly
|  | powerclear | 电量清零 | 0x8004 | uint8_t | 1 | writeonly
|  | eventclear | 事件总清 | 0x8005 | uint8_t | 1 | writeonly
|  | operationclear | 运行信息清零 | 0x8006 | uint8_t | 1 | writeonly
|  | reset_run_timeout | 复位运行超时 | 0x8007 | uint8_t | 1 | writeonly
|  | reset_fault_number | 复位故障次数 | 0x8008 | uint8_t | 1 | writeonly
|  | flashclear | 恢复出厂 | 0x8009 | uint8_t | 1 | writeonly
event_log | 保护事件 | fault_data | (上1次)故障原因 | 0x9000 | uint8_t | 1 | readonly
|  | fault_phase | (上1次)故障相别 | 0x9001 | uint8_t | 1 | readonly
|  | fault_time | (上1次)跳闸发生时刻 | 0x9002 | uint8_t | 6 | readonly
|  | voltage_A | (上1次)跳闸前A相电压 | 0x9005 | uint16_t | 2 | readonly
|  | voltage_B | (上1次)跳闸前B相电压 | 0x9006 | uint16_t | 2 | readonly
|  | voltage_C | (上1次)跳闸前C相电压 | 0x9007 | uint16_t | 2 | readonly
|  | current_A | (上1次)跳闸前A相电流 | 0x9008 | float | 4 | readonly
|  | current_B | (上1次)跳闸前B相电流 | 0x900A | float | 4 | readonly
|  | current_C | (上1次)跳闸前C相电流 | 0x900C | float | 4 | readonly
|  | leakage | (上1次)跳闸前漏电电流 | 0x900E | float | 4 | readonly
|  | current_ground | (上1次)跳闸前接地电流 | 0x9010 | float | 4 | readonly
|  | Active_Power | (上1次)跳闸前总有功率 | 0x9012 | float | 4 | readonly
|  | standby | 备用 | 0x9014 | uint16_t | 2 | readonly
………………………………………
|  | fault_data | (上10次)故障原因 | 0x90BD | uint8_t | 1 | readonly
|  | fault_phase | (上10次)故障相别 | 0x90BE | uint8_t | 1 | readonly
|  | fault_time | (上10次)跳闸发生时刻 | 0x90BF | uint8_t | 6 | readonly
|  | voltage_A | (上10次)跳闸前A相电压 | 0x90C2 | uint16_t | 2 | readonly
|  | voltage_B | (上10次)跳闸前B相电压 | 0x90C3 | uint16_t | 2 | readonly
|  | voltage_C | (上10次)跳闸前C相电压 | 0x90C4 | uint16_t | 2 | readonly
|  | current_A | (上10次)跳闸前A相电流 | 0x90C5 | float | 4 | readonly
|  | current_B | (上10次)跳闸前B相电流 | 0x90C7 | float | 4 | readonly
|  | current_C | (上10次)跳闸前C相电流 | 0x90C9 | float | 4 | readonly
|  | leakage | (上10次)跳闸前漏电电流 | 0x90CB | float | 4 | readonly
|  | current_ground | (上10次)跳闸前接地电流 | 0x90CD | float | 4 | readonly
|  | Active_Power | (上10次)跳闸前总有功率 | 0x90CF | float | 4 | readonly
|  | standby | 备用 | 0x90D1 | uint16_t | 6 | readonly
| 告警事件 | state | (上1次)状态 | 0x9100 | uint8_t | 1 | readonly
|  | fault_data | (上1次)故障原因 | 0x9101 | uint8_t | 1 | readonly
|  | fault_phase | (上1次)故障相别 | 0x9102 | uint8_t | 2 | readonly
|  | fault_time | (上1次)告警发生时刻 | 0x9103 | uint8_t | 6 | readonly
|  | voltage_A | (上1次)告警前A相电压 | 0x9106 | uint16_t | 2 | readonly
|  | voltage_B | (上1次)告警前B相电压 | 0x9107 | uint16_t | 2 | readonly
|  | voltage_C | (上1次)告警前C相电压 | 0x9108 | uint16_t | 2 | readonly
|  | current_A | (上1次)告警前A相电流 | 0x9109 | float | 4 | readonly
|  | current_B | (上1次)告警前B相电流 | 0x910B | float | 4 | readonly
|  | current_C | (上1次)告警前C相电流 | 0x910D | float | 4 | readonly
|  | leakage | (上1次)告警前漏电电流 | 0x910F | float | 4 | readonly
|  | current_ground | (上1次)告警前接地电流 | 0x9111 | float | 4 | readonly
|  | Active_Power | (上1次)告警前总有功率 | 0x9113 | float | 4 | readonly
|  | standby | 备用 | 0x9115 | uint16_t | 2 | readonly
………………………………………
|  | state | (上10次)状态 | 0x91C6 | uint8_t | 1 | readonly
|  | fault_data | (上10次)故障原因 | 0x91C7 | uint8_t | 1 | readonly
|  | fault_phase | (上10次)故障相别 | 0x91C8 | uint8_t | 2 | readonly
|  | fault_time | (上10次)告警发生时刻 | 0x91C9 | uint8_t | 6 | readonly
|  | voltage_A | (上10次)告警前A相电压 | 0x91CC | uint16_t | 2 | readonly
|  | voltage_B | (上10次)告警前B相电压 | 0x91CD | uint16_t | 2 | readonly
|  | voltage_C | (上10次)告警前C相电压 | 0x91CE | uint16_t | 2 | readonly
|  | current_A | (上10次)告警前A相电流 | 0x91CF | float | 4 | readonly
|  | current_B | (上10次)告警前B相电流 | 0x91D1 | float | 4 | readonly
|  | current_C | (上10次)告警前C相电流 | 0x91D3 | float | 4 | readonly
|  | leakage | (上10次)告警前漏电电流 | 0x91D5 | float | 4 | readonly
|  | current_ground | (上10次)告警前接地电流 | 0x91D7 | float | 4 | readonly
|  | Active_Power | (上10次)告警前总有功率 | 0x91D9 | float | 4 | readonly
|  | standby | 备用 | 0x91DB | uint16_t | 2 | readonly
| 操作事件 | state | (上1次)状态 | 0x9200 | uint8_t | 1 | readonly
|  | operate_data | (上1次)操作方式 | 0x9201 | uint8_t | 1 | readonly
|  | fault_time | (上1次)操作发生时刻 | 0x9202 | uint8_t | 6 | readonly
………………………………………
|  | state | (上10次)状态 | 0x922D | uint8_t | 1 | readonly
|  | operate_data | (上10次)操作方式 | 0x922E | uint8_t | 1 | readonly
|  | fault_time | (上10次)操作发生时刻 | 0x922F | uint8_t | 6 | readonly
| DI事件 | state | (上1次)状态 | 0x9500 | uint16_t | 1 | readonly
|  | channel | (上1次)通道 | 0x9501 | uint16_t | 1 | readonly
|  | fault_time | (上1次)发生时刻 | 0x9502 | uint16_t | 6 | readonly
………………………………………
|  | state | (上10次)状态 | 0x952D | uint16_t | 1 | readonly
|  | channel | (上10次)通道 | 0x952E | uint16_t | 1 | readonly
|  | fault_time | (上10次)发生时刻 | 0x952F | uint16_t | 6 | readonly
| DO事件 | state | (上1次)状态 | 0x9600 | uint16_t | 1 | readonly
|  | channel | (上1次)通道 | 0x9601 | uint16_t | 1 | readonly
|  | fault_time | (上1次)发生时刻 | 0x9602 | uint16_t | 6 | readonly
………………………………………
|  | state | (上10次)状态 | 0x962D | uint16_t | 1 | readonly
|  | channel | (上10次)通道 | 0x962E | uint16_t | 1 | readonly
|  | fault_time | (上10次)发生时刻 | 0x962F | uint16_t | 6 | readonly
SYSTEM_PARAMETER | 运行数据 | run_time_now | 本次运行时间 | 0x2000 | uint32_t | 4 | readonly
|  | stop_time_now | 本次停车时间 | 0x2002 | uint32_t | 4 | readonly
|  | run_time_all | 总运行时间 | 0x2004 | uint32_t | 4 | readonly
|  | stop_time_all | 总停车时间 | 0x2006 | uint32_t | 4 | readonly
|  | start_number | 起动次数 | 0x2008 | uint32_t | 4 | readonly
|  | trip_number | 脱扣次数 | 0x200A | uint32_t | 4 | readonly
|  | start_current_max | 最大起动电流 | 0x200C | float | 4 | readonly
|  | run_current_max | 最大运行电流 | 0x200E | float | 4 | readonly
| 系统参数 | work_mode | 工作模式 | 0x4000 | uint8_t | 1 | readwrite
|  | rated_current_type | 额定电流规格 | 0x4001 | uint16_t | 2 | readonly
|  | rated_current | 额定电流 | 0x4002 | uint16_t | 2 | readwrite
|  | rated_voltage_type | 额定电压 | 0x4003 | uint16_t | 2 | readwrite
|  | rated_power | 额定功率 | 0x4004 | uint32_t | 4 | readwrite
|  | rated_freq | 额定频率 | 0x4006 | uint8_t | 1 | readwrite
|  | motor_type | 电机类型 | 0x4007 | uint8_t | 1 | readwrite
|  | rated_current_high | 额定电流（高速） | 0x4008 | uint16_t | 2 | readwrite
|  | rated_power_high | 额定功率（高速） | 0x4009 | uint32_t | 4 | readwrite
|  | connection | 接线方式 | 0x400B | uint8_t | 1 | readwrite
|  | ct_scale | CT变比 | 0x400C | uint8_t | 1 | readwrite
|  | protect_selec | 保护选择 | 0x400D | uint8_t | 1 | readwrite
|  | language | 语言 | 0x400E | uint8_t | 1 | readwrite
|  | backlight | 背光 | 0x400F | uint8_t | 1 | readwrite
|  | setup | 液晶对比度 | 0x4010 | uint8_t | 1 | readwrite
|  | password | 液晶密码 | 0x4011 | uint16_t | 2 | readwrite
|  | time_set[7] | 时间设置 | 0x4012 | 7个字节 | 7 | readwrite
|  | SOFT_VER | 软件版本 | 0x4019 | 10个字节 | 10 | readonly
|  | HARD_VER | 硬件版本 | 0x4023 | 6个字节 | 6 | readonly
|  | timed_record_en | 启动方式（定时记录） | 0x4100 | uint8_t | 1 | readwrite
|  | timed_record_mode | 记录模式（定时记录） | 0x4101 | uint8_t | 1 | readwrite
|  | timed_record_time | 记录间隔（定时记录） | 0x4102 | uint16_t | 2 | readwrite
|  | modbus_addr[0] | 通讯modbus1地址 | 0x4500 | uint8_t | 1 | readwrite
|  | modbus_baud[0] | 通讯modbus1波特率 | 0x4501 | uint16_t | 2 | readwrite
|  | modbus_check[0] | 通讯modbus1校验 | 0x4502 | uint8_t | 1 | readwrite
|  | modbus_addr[1] | 通讯modbus2地址 | 0x4503 | uint8_t | 1 | readwrite
|  | modbus_baud[1] | 通讯modbus2波特率 | 0x4504 | uint16_t | 2 | readwrite
|  | modbus_check[1] | 通讯modbus2校验 | 0x4505 | uint8_t | 1 | readwrite
|  | can_addr | 通讯can地址 | 0x4506 | uint8_t | 1 | readwrite
|  | can_baud | 通讯can波特率 | 0x4507 | uint16_t | 2 | readwrite
|  | can_check | 通讯can校验 | 0x4508 | uint8_t | 1 | readwrite
|  | transmit_type[0] | 变送器1设置类型 | 0x4509 | uint8_t | 1 | readwrite
|  | transmit_threshold[0] | 变送器1设置阈值 | 0x450A | uint16_t | 2 | readwrite
|  | transmit_type[1] | 变送器2设置类型 | 0x450B | uint8_t | 1 | readwrite
|  | transmit_threshold[1] | 变送器2设置阈值 | 0x450C | uint16_t | 2 | readwrite
|  | transmit_type[2] | 变送器3设置类型 | 0x450D | uint8_t | 1 | readwrite
|  | transmit_threshold[2] | 变送器3设置阈值 | 0x450E | uint16_t | 2 | readwrite
|  | transmit_type[3] | 变送器4设置类型 | 0x450F | uint8_t | 1 | readwrite
|  | transmit_threshold[3] | 变送器4设置阈值 | 0x4510 | uint16_t | 2 | readwrite
| 控制数据 | control_type | 控制权限 | 0x6000 | uint8_t | 1 | readwrite
|  | control_start_type | 起动模式 | 0x6001 | uint8_t | 1 | readwrite
|  | voltage_start_type | 切换时序（降压启动） | 0x6002 | uint8_t | 1 | readwrite
|  | voltage_start1_delay | 起动1延时（降压启动） | 0x6003 | uint16_t | 2 | readwrite
|  | voltage_start_current | 切换电流（降压启动） | 0x6004 | uint16_t | 2 | readwrite
|  | way_start_type | 工作模式（双向启动） | 0x6005 | uint8_t | 1 | readwrite
|  | way_start_switch_delay | 切换延时（双向启动） | 0x6006 | uint16_t | 2 | readwrite
|  | way_start_corotation_delay | 正转延时（双向启动） | 0x6007 | uint16_t | 2 | readwrite
|  | way_start_reversal_delay | 反转延时（双向启动） | 0x6008 | uint16_t | 2 | readwrite
|  | speed_start_delay | 切换延时（双速启动） | 0x6009 | uint16_t | 2 | readwrite
|  | speed_start_current | 切换电流（双速启动） | 0x600A | uint16_t | 2 | readwrite
|  | start_automatic_mode | 自起动模式 | 0x600B | uint8_t | 1 | readwrite
|  | start_automatic_delay | 自起动延时 | 0x600C | uint16_t | 2 | readwrite
|  | start_automatic_en | 自起动使能 | 0x600D | uint8_t | 1 | readwrite
|  | loss_voltage_restore | 失压恢复电压 | 0x600E | uint8_t | 1 | readwrite
|  | loss_voltage_drop | 失压跌落电压 | 0x600F | uint8_t | 1 | readwrite
|  | loss_voltage_delay | 晃电时间 | 0x6010 | uint8_t | 1 | readwrite
|  | loss_voltage_allow_delay | 失压允许时间 | 0x6011 | uint16_t | 2 | readwrite
|  | loss_voltage_restart_delay | 失压重启延时 | 0x6012 | uint16_t | 2 | readwrite
|  | loss_voltage_restart_en | 失压重启使能 | 0x6013 | uint8_t | 1 | readwrite
|  | DI_type[0] | DI1类型 | 0x6014 | uint8_t | 1 | readwrite
|  | DI_mode[0] | DI1定义 | 0x6015 | uint8_t | 1 | readwrite
|  | DI_type[1] | DI2类型 | 0x6016 | uint8_t | 1 | readwrite
|  | DI_mode[1] | DI2定义 | 0x6017 | uint8_t | 1 | readwrite
|  | DI_type[2] | DI3类型 | 0x6018 | uint8_t | 1 | readwrite
|  | DI_mode[2] | DI3定义 | 0x6019 | uint8_t | 1 | readwrite
|  | DI_type[3] | DI4类型 | 0x601A | uint8_t | 1 | readwrite
|  | DI_mode[3] | DI4定义 | 0x601B | uint8_t | 1 | readwrite
|  | DI_type[4] | DI5类型 | 0x601C | uint8_t | 1 | readwrite
|  | DI_mode[4] | DI5定义 | 0x601D | uint8_t | 1 | readwrite
|  | DI_type[5] | DI6类型 | 0x601E | uint8_t | 1 | readwrite
|  | DI_mode[5] | DI6定义 | 0x601F | uint8_t | 1 | readwrite
|  | DO_mode[0] | DO1定义 | 0x6020 | uint8_t | 1 | readwrite
|  | DO_delay[0] | DO1脉冲时间 | 0x6021 | uint16_t | 2 | readwrite
|  | DO_mode[1] | DO2定义 | 0x6022 | uint8_t | 1 | readwrite
|  | DO_delay[1] | DO2脉冲时间 | 0x6023 | uint16_t | 2 | readwrite
|  | DO_mode[2] | DO3定义 | 0x6024 | uint8_t | 1 | readwrite
|  | DO_delay[2] | DO3脉冲时间 | 0x6025 | uint16_t | 2 | readwrite
|  | DO_mode[3] | DO4定义 | 0x6026 | uint8_t | 1 | readwrite
|  | DO_delay[3] | DO4脉冲时间 | 0x6027 | uint16_t | 2 | readwrite
| 调试数据 DEVICE_SET_PARAMETER | debug_mode_DI | DI模拟配置 | 0x7000 | uint8_t | 1 | readwrite
|  | DI_state_simulate[0] | 模拟DI1 | 0x7001 | uint8_t | 1 | readwrite
|  | DI_state_simulate[1] | 模拟DI2 | 0x7002 | uint8_t | 1 | readwrite
|  | DI_state_simulate[2] | 模拟DI3 | 0x7003 | uint8_t | 1 | readwrite
|  | DI_state_simulate[3] | 模拟DI4 | 0x7004 | uint8_t | 1 | readwrite
|  | DI_state_simulate[4] | 模拟DI5 | 0x7005 | uint8_t | 1 | readwrite
|  | DI_state_simulate[5] | 模拟DI6 | 0x7006 | uint8_t | 1 | readwrite
|  | debug_mode_DO | DO模拟配置 | 0x7007 | uint8_t | 1 | readwrite
|  | DO_state_simulate[0] | 模拟DO1 | 0x7008 | uint8_t | 1 | readwrite
DEVICE_SET_PARAMETER |  | DO_state_simulate[1] | 模拟DO2 | 0x7009 | uint8_t | 1 | readwrite
|  | DO_state_simulate[2] | 模拟DO3 | 0x700A | uint8_t | 1 | readwrite
|  | DO_state_simulate[3] | 模拟DO4 | 0x700B | uint8_t | 1 | readwrite
|  | Power_Fac_simulate | 模拟功率因素 | 0x700C | float | 4 | readwrite
|  | Current_simulate_A | 模拟A相电流 | 0x700E | uint16_t | 2 | readwrite
|  | Current_simulate_B | 模拟B相电流 | 0x700F | uint16_t | 2 | readwrite
|  | Current_simulate_C | 模拟C相电流 | 0x7010 | uint16_t | 2 | readwrite
|  | Total_Creepage_simulate | 模拟漏电流 | 0x7011 | uint16_t | 2 | readwrite
|  | Current_Ground_simulate | 模拟接地电流 | 0x7012 | uint16_t | 2 | readwrite
|  | Voltage_simulate_A | 模拟A相电压 | 0x7013 | uint16_t | 2 | readwrite
|  | Voltage_simulate_B | 模拟B相电压 | 0x7014 | uint16_t | 2 | readwrite
|  | Voltage_simulate_C | 模拟C相电压 | 0x7015 | uint16_t | 2 | readwrite
MANUFACTURER_PARAMETER | 厂内参数 | rated_current_type | 额定电流规格 | 0xE000 | uint16_t | 2 | readwrite
|  | main_type | 主型选择 | 0xE001 | uint8_t | 1 | readwrite
|  | leakage_ct | 漏电变比 | 0xE002 | uint8_t | 1 | readwrite
|  | meter_mode | 校表模式 | 0xE003 | uint8_t | 1 | readwrite
|  | anti_shock_mode | 抗晃电模式 | 0xE004 | uint8_t | 1 | readwrite
|  | extension_mode | 扩展模式 | 0xE005 | uint8_t | 1 | readwrite
| 校表参数（还在和设备讨论中） | 校表流程：1.先写入校表参数 2.启动校表 3.电流偏置 4.开始校表 5.结束校表
|  | device.check_curgain | 电流增益（输入电流值） | 0xF002 | float | 4
|  | device.check_curfare | 电流增益（校表通道） | 0xF004 | uint16_t | 2 | 0： ABC三通道 1：N通道 2：其他电流通道
|  | device.check_curgain2 | 第二段电流增益（输入电流值） | 0xF005 | float | 4
|  | device.check_curfare2 | 第二段电流增益（校表通道） | 0xF007 | uint16_t | 2 | 0： ABC三通道 1：N通道 2：其他电流通道
|  | device.check_volgain | 电压增益（输入电压值） | 0xF008 | float | 4
|  | device.check_powergain | 功率增益（输入功率值） | 0xF00A | float | 4
|  | device.check_powerfac | 功率增益（功率因素） | 0xF00C | float | 4
|  | bool caliStart(void) | 启动校表 | 0xF000 | uint16_t | 2
|  | bool caliCurOffset(void) | 电流偏置 | 0xF001 | uint16_t | 2
|  | start_meter | 开始校表 | 0xF00F | uint16_t | 2
|  | bool caliStop(void) | 结束校准 | 0xF00E | uint16_t | 2